## Guide
AHIM: Master Asset Register & Common Record
Asset Health & Integrity Management · Lotus Africa Uranium Plant
Purpose
Every inspection input (vibration and visual routes, IR, substation, statutory, ultrasonic, oil analysis, diesel generator checklists, light vehicle and heavy equipment inspections and prestarts) is entered in ONE format against ONE asset list. The register and records then feed the AHIM dashboard: plant health, criticality, top priorities, open records and machine history.
How it works
Step | What to do | Who
1. Register the asset | Add it to Asset_Register with its Pronto asset no., area, class, criticality factors and applicable techniques. ACI and class calculate automatically. | RCM Specialist (once per asset)
2. Enter the result | Each reading, checklist defect or certificate check becomes one row in Records. Pick the asset from the dropdown; description, area and ACI fill in. | Input owner (analyst, electrician, DG operator, fleet mechanic, contractor)
3. Status is set | Measured values: from the Alert/Danger limits. Checklists, visual, statutory: Inspector status using the severity rules below. | Automatic / inspector
4. Priority and due date | Alert and Danger rows get a priority score (ACI x severity), P1/P2/P3 and a due date automatically. Any Danger is always P1, whatever the asset criticality. | Automatic
5. Action and close | Raise the Pronto WO, enter the WO no., move the stage forward. Close only after a re-check confirms the fix, and record who verified it. | RCM Specialist / planner
6. Review | The asset's Current status in the register always shows the worst open record. Use filters on Records for overdue items. | RCM Specialist (weekly)
Colour legend
Item | Meaning
Dark blue header | Enter data in this column
Grey header, grey cells | Automatic formula: do not type over
Blue italic text | Sample data: replace or delete before go-live
Blue on cream (Lists sheet) | Settings: weights, thresholds, response times
Red key cell (register) | Duplicate Pronto asset no.
Amber Record stage | Alert/Danger row with no stage yet
How each input source maps into the record
Source (input) | Technique(s) | Record type | How status is set | Typical frequency | Owner
Vibration & visual route | Vibration, Visual | Measured + checklist | Limits (ISO 20816-3: 4.5 / 7.1 mm/s); visual by severity rules | Monthly route | RCM Specialist
IR survey | Infrared | Measured | dT limits (NETA: >4 °C Alert, >15 °C Danger) or absolute temperature limits | Monthly | RCM Specialist
Substation inspection | Infrared, Visual, Electrical | Measured + checklist | Limits for readings; severity rules for checklist items | Monthly | Electrical
Statutory inspection | Statutory | Compliance | Inspector status; register also flags expiry (60 days = Alert, expired = Danger) | Per certificate | RCM Specialist / contractor
Ultrasonic report | Ultrasonic thickness, Ultrasonics (airborne) | Measured | Thickness: Lower is worse vs minimum wall. Airborne: dB limits | Quarterly / annual | UT contractor / RCM
Oil analysis | Lubrication / oil | Measured | Lab alarm limits per parameter (water, iron, silicon, viscosity...) | Monthly / per service | RCM Specialist
DG checklist | DG checks | Measured | Enter only the condition parameters (exhaust and turbo temperatures, oil pressure, coolant temperature, crankcase pressure) with limits | Daily; enter weekly summary or any exceedance | DG operator
LV/HV inspection checklist | Fleet inspection | Checklist | Severity rules per component | Per service / monthly | Fleet mechanic
LV/HV prestart checklist | Prestart | Exceptions only | Enter only defects found (severity rules); completion rate tracked separately | Every shift | Operator / supervisor
Severity rules for checklists, visual and prestart items
Status | Definition | Required response | Examples
OK | Item within standard | None (record only if part of a route) | Guards fitted, no leaks
Alert | Defect, but safe to operate | Repair within P2/P3 response time | Minor oil leak, silica gel discoloured, worn seat, reverse alarm faulty
Danger | Unsafe or failure imminent | Stop / isolate / tag out; repair before use (P1) | Brakes or steering ineffective, seatbelt or fire suppression faulty, major leak, exposed live parts
Asset numbering convention (site tag)
Prefix | Area | Example
AP- | Acid plant | AP-P-101 (pump), AP-TK-01 (tank)
CK- | Calciner | CK-1080
SS- | Substation | SS-TX-01, SS-MCC-01
PP- | Power plant | PP-GEN-04
LV- / HV- | Mobile fleet | LV-01 light vehicle, HV-02 compactor
The Pronto asset no. remains the unique key; the site tag is the name people use in the field. Sample Pronto numbers (1001xx...) are placeholders.
Repeat readings rule
Each new reading is a new row. If a reading repeats an issue already raised in an earlier row, set its Record stage to "No action": it updates the trend and the asset status, but does not create a second open recommendation. An asset returns to OK when its recommendation is Closed and the latest reading is within limits.
Dashboard sheets
Sheet | Feeds
Events | Machine history, MTBF/MTTR, availability, bad actors (Pronto WO export)
Schedule | Inspection schedule compliance
CM_Value / Programme_Cost | CM return on investment
Decisions | Management decisions required
Prestart | Fleet prestart compliance
Settings (Lists sheet)
ACI weights, criticality class limits, priority bands and response times (P1 7 days, P2 30, P3 60), severity factors (Danger 1.0, Alert 0.6) and the statutory alert window (60 days) are editable on the Lists sheet. Get them approved by the Engineering Manager before go-live so the numbers are not disputed.

## Asset_Register
AHIM Master Asset Register
Dark headers = enter data. Grey headers = automatic (do not type). Blue italic rows are SAMPLES: replace with the Pronto asset list. Pronto asset no. is the unique key used everywhere.
[11 empty] | Criticality factors: 1 = low impact, 5 = severe | [8 empty] | Applicable techniques (enter Y)
Pronto asset no. | Site tag | Description | Area | System / location | Asset class | Manufacturer | Model | Serial no. | Operating mode | Asset state | Safety & env. (1-5) | Production (1-5) | Redundancy (1-5) | Repair cost / MTTR (1-5) | Failure history (1-5) | ACI (0-100) | Class | Current status | Open records | Vibration | Lubrication / oil | Ultrasonics (airborne) | Ultrasonic thickness | Infrared | Visual | Statutory | Tank & vessel | Piping | Structural | Electrical | DG checks | Fleet inspection | Prestart | Statutory cert. required | Certificate expiry | Days to expiry | Statutory status | Responsible | Remarks | Strategy class | Consequence (1-5) | Service | Bottleneck (Y/N) | Replacement value (USD) | Consequence basis | Install year | Design life (years)
100101 | AP-SF-01 | Sulphur furnace | Acid plant | Gas generation | Fired equipment |  |  |  | Duty | Active | 5 | 5 | 5 | 5 | 2 | 94 | A | Danger | 1 |  |  |  |  | Y | Y | Y |  |  | Y |  |  |  |  | Y | 2027-03-18 | 164 | OK | Mechanical |  | Sulphur furnace / refractory-lined equipment | 5 |  |  | 6000000 | Default: criticality factors (safety and environment 5, production 5) | 2008 | 30
100102 | AP-WHB-01 | Waste heat boiler | Acid plant | Gas generation | Boiler |  |  |  | Duty | Active | 5 | 5 | 5 | 4 | 2 | 91 | A | Alert | 1 |  |  | Y | Y | Y | Y | Y | Y | [6 empty] | Y | 2026-10-22 | 17 | Alert | Mechanical |  | Pressure vessel / boiler | 5 |  |  | 4500000 | Default: criticality factors (safety and environment 5, production 5) | 2008 | 25
100103 | AP-BL-01 | Main air blower | Acid plant | Gas generation | Rotating - fan / blower |  |  |  | Duty | Active | 4 | 5 | 5 | 4 | 3 | 87 | A | Alert | 1 | Y | Y | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Mechanical |  | Fan / blower | 5 |  |  | 2200000 | Default: criticality factors (safety and environment 4, production 5) | 2008 | 25
100104 | AP-CV-01 | SO2 converter | Acid plant | Conversion | Pressure vessel |  |  |  | Duty | Active | 4 | 5 | 5 | 5 | 1 | 86 | A | Alert | 3 |  |  |  |  | Y | Y |  | Y |  | Y |  |  |  |  | N |  |  |  | Mechanical |  | Pressure vessel / boiler | 5 |  |  | 5000000 | Default: criticality factors (safety and environment 4, production 5) | 2008 | 30
100105 | AP-P-101 | Drying tower acid pump | Acid plant | Drying & absorption | Rotating - pump |  |  |  | Duty | Active | 4 | 4 | 3 | 3 | 4 | 74 | A | Danger | 2 | Y | Y | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Mechanical |  | Centrifugal process pump | 4 |  |  | 180000 | Default: criticality factors (safety and environment 4, production 4) | 2012 | 15
100106 | AP-P-102 | Interpass tower acid pump | Acid plant | Drying & absorption | Rotating - pump |  |  |  | Duty | Active | 4 | 5 | 3 | 3 | 2 | 76 | A | OK | 0 | Y | Y | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Mechanical |  | Centrifugal process pump | 5 |  |  | 180000 | Default: criticality factors (safety and environment 4, production 5) | 2012 | 15
100107 | AP-P-103 | Final tower acid pump | Acid plant | Drying & absorption | Rotating - pump |  |  |  | Duty | Active | 3 | 4 | 3 | 3 | 3 | 66 | B | Alert | 5 | Y | Y | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Mechanical |  | Centrifugal process pump | 4 |  |  | 160000 | Default: criticality factors (safety and environment 3, production 4) | 2009 | 15
100108 | AP-P-201 | Boiler feed water pump A | Acid plant | Steam system | Rotating - pump |  |  |  | Duty | Active | 4 | 5 | 2 | 3 | 3 | 75 | A | Alert | 1 | Y | Y | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Mechanical |  | Centrifugal process pump | 5 |  |  | 140000 | Default: criticality factors (safety and environment 4, production 5) | 2010 | 20
100109 | AP-P-202 | Boiler feed water pump B | Acid plant | Steam system | Rotating - pump |  |  |  | Standby | Active | 4 | 5 | 2 | 3 | 1 | 71 | A | OK | 0 | Y | Y | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Mechanical |  | Centrifugal process pump | 5 |  |  | 140000 | Default: criticality factors (safety and environment 4, production 5) | 2010 | 20
100110 | AP-P-301 | Molten sulphur pump | Acid plant | Sulphur handling | Rotating - pump |  |  |  | Duty | Active | 3 | 4 | 3 | 2 | 2 | 61 | B | OK | 0 | Y | Y | Y |  | Y | Y | [8 empty] | N |  |  |  | Mechanical |  | Centrifugal process pump | 4 |  |  | 120000 | Default: criticality factors (safety and environment 3, production 4) | 2008 | 20
100111 | AP-AG-01 | Sulphur melter agitator | Acid plant | Sulphur handling | Rotating - agitator |  |  |  | Duty | Active | 2 | 2 | 3 | 2 | 2 | 43 | C | OK | 0 | Y | Y |  |  |  | Y | [8 empty] | N |  |  |  | Mechanical |  | Agitator | 2 |  |  | 90000 | Default: criticality factors (safety and environment 2, production 2) | 2008 | 20
100112 | AP-CT-01 | Cooling tower fan 1 | Acid plant | Cooling water | Rotating - gearbox / drive |  |  |  | Duty | Active | 2 | 3 | 2 | 2 | 4 | 50 | B | Alert | 10 | Y | Y |  |  |  | Y |  |  |  | Y | Y |  |  |  | N |  |  |  | Mechanical |  | Gearbox (stand-alone) | 3 |  |  | 350000 | Default: criticality factors (safety and environment 2, production 3) | 2008 | 20
100113 | AP-TK-01 | Product acid storage tank | Acid plant | Product storage | Tank |  |  |  | Duty | Active | 5 | 3 | 4 | 4 | 2 | 76 | A | Alert | 2 |  |  |  | Y |  | Y | Y | Y |  | Y |  |  |  |  | Y | 2027-04-02 | 179 | OK | Mechanical |  | Atmospheric storage tank | 5 |  |  | 1200000 | Default: criticality factors (safety and environment 5, production 3) | 2008 | 25
100114 | AP-PL-01 | Acid transfer line | Acid plant | Product storage | Piping |  |  |  | Duty | Active | 5 | 4 | 5 | 2 | 3 | 81 | A | Danger | 1 |  |  |  | Y |  | Y |  |  | Y | [5 empty] | N |  |  |  | Mechanical |  | Piping (acid / slurry / process) | 5 |  |  | 300000 | Default: criticality factors (safety and environment 5, production 4) | 2011 | 15
100115 | AP-AR-01 | Instrument air receiver | Acid plant | Utilities air | Pressure vessel |  |  |  | Duty | Active | 4 | 2 | 3 | 2 | 1 | 53 | B | OK | 0 |  |  | Y |  |  | Y | Y | Y | [6 empty] | Y | 2027-03-12 | 158 | OK | Mechanical |  | Pressure vessel / boiler | 4 |  |  | 80000 | Default: criticality factors (safety and environment 4, production 2) | 2008 | 30
100201 | CK-1080 | Calciner kiln 1080 | Calciner | Calcining | Rotary kiln |  |  |  | Duty | Active | 4 | 5 | 5 | 5 | 3 | 90 | A | Alert | 2 | Y | Y |  |  | Y | Y |  |  |  | Y |  |  |  |  | N |  |  |  | Mechanical |  | Rotary dryer / kiln / calciner | 5 |  |  | 12000000 | Default: criticality factors (safety and environment 4, production 5) | 2009 | 30
100301 | SS-TX-01 | Transformer TX-01 | Substation | Main substation | Electrical - transformer |  |  |  | Duty | Active | 4 | 5 | 5 | 5 | 1 | 86 | A | Alert | 4 |  | Y | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Electrical |  | Switchgear / MCC / transformer | 5 |  |  | 1500000 | Default: criticality factors (safety and environment 4, production 5) | 2008 | 35
100302 | SS-MCC-01 | Acid plant MCC | Substation | Main substation | Electrical - switchgear / MCC |  |  |  | Duty | Active | 4 | 5 | 5 | 3 | 2 | 82 | A | Danger | 2 |  |  | Y |  | Y | Y |  |  |  |  | Y |  |  |  | N |  |  |  | Electrical |  | Switchgear / MCC / transformer | 5 |  |  | 600000 | Default: criticality factors (safety and environment 4, production 5) | 2008 | 25
100401 | PP-GEN-01 | Diesel generator Gen 1 | Power plant | Power station | Diesel generator | Hyundai |  |  | Duty | Active | 4 | 5 | 3 | 4 | 4 | 83 | A | Alert | 1 | Y | Y |  |  | Y | Y |  |  |  |  | Y | Y |  |  | N |  |  |  | Power plant |  | Diesel generator | 5 |  |  | 1800000 | Default: criticality factors (safety and environment 4, production 5) | 2010 | 20
100402 | PP-GEN-02 | Diesel generator Gen 2 | Power plant | Power station | Diesel generator | Hyundai |  |  | Duty | Active | 4 | 5 | 3 | 4 | 2 | 79 | A | OK | 0 | Y | Y |  |  | Y | Y |  |  |  |  | Y | Y |  |  | N |  |  |  | Power plant |  | Diesel generator | 5 |  |  | 1800000 | Default: criticality factors (safety and environment 4, production 5) | 2010 | 20
100403 | PP-GEN-03 | Diesel generator Gen 3 | Power plant | Power station | Diesel generator | Hyundai |  |  | Standby | Active | 4 | 5 | 3 | 4 | 2 | 79 | A | OK | 0 | Y | Y |  |  | Y | Y |  |  |  |  | Y | Y |  |  | N |  |  |  | Power plant |  | Diesel generator | 5 |  |  | 1800000 | Default: criticality factors (safety and environment 4, production 5) | 2010 | 20
100404 | PP-GEN-04 | Diesel generator Gen 4 | Power plant | Power station | Diesel generator | Hyundai |  |  | Duty | Active | 5 | 5 | 3 | 5 | 4 | 92 | A | Alert | 1 | Y | Y |  |  | Y | Y |  |  |  |  | Y | Y |  |  | N |  |  |  | Power plant |  | Diesel generator | 5 |  |  | 1800000 | Default: criticality factors (safety and environment 5, production 5) | 2010 | 20
100501 | LV-01 | Light vehicle LV-01 (pickup) | Mobile fleet | Light vehicles | Light vehicle |  |  |  | Mobile | Active | 3 | 2 | 2 | 1 | 2 | 43 | C | Alert | 1 |  | Y |  |  |  | Y | [6 empty] | Y | Y | N |  |  |  | Fleet workshop |  |  | 3 |  |  | 60000 | Default: criticality factors (safety and environment 3, production 2) | 2021 | 6
100502 | LV-02 | Light vehicle LV-02 (pickup) | Mobile fleet | Light vehicles | Light vehicle |  |  |  | Mobile | Active | 3 | 2 | 2 | 1 | 1 | 41 | C | OK | 0 |  | Y |  |  |  | Y | [6 empty] | Y | Y | N |  |  |  | Fleet workshop |  |  | 3 |  |  | 60000 | Default: criticality factors (safety and environment 3, production 2) | 2022 | 6
100601 | HV-01 | Dozer HV-01 | Mobile fleet | Heavy equipment | Heavy equipment |  |  |  | Mobile | Active | 4 | 3 | 3 | 4 | 3 | 69 | B | Alert | 1 |  | Y |  |  |  | Y | [6 empty] | Y | Y | N |  |  |  | Fleet workshop |  |  | 4 |  |  | 900000 | Default: criticality factors (safety and environment 4, production 3) | 2015 | 12
100602 | HV-02 | Compactor HV-02 | Mobile fleet | Heavy equipment | Heavy equipment |  |  |  | Mobile | Active | 4 | 2 | 3 | 3 | 2 | 58 | B | Danger | 1 |  | Y |  |  |  | Y | [6 empty] | Y | Y | N |  |  |  | Fleet workshop |  |  | 4 |  |  | 450000 | Default: criticality factors (safety and environment 4, production 2) | 2016 | 12
100603 | HV-03 | Front-end loader HV-03 | Mobile fleet | Heavy equipment | Heavy equipment |  |  |  | Mobile | Active | 4 | 3 | 3 | 4 | 2 | 67 | B | Alert | 1 |  | Y |  |  |  | Y | [6 empty] | Y | Y | N |  |  |  | Fleet workshop |  |  | 4 |  |  | 700000 | Default: criticality factors (safety and environment 4, production 3) | 2017 | 12
Formulas:
Days to expiry = IF([Certificate expiry]="","",[Certificate expiry]-TODAY())
Note on A4: Unique key. Use the asset number exactly as in Pronto so records link to work orders. Duplicates turn red.
Note on S4: Worst status among this asset's records that are not Closed. "No data" = no record yet.

## Records
AHIM Common Record
One row per reading, checklist defect or certificate check, from ANY source. Dark headers = enter. Grey = automatic. Blue italic rows are SAMPLES showing each source: delete them before go-live.
Record ID | Date | Pronto asset no. | Description | Area | Class | ACI | Source (input) | Technique | Component / parameter / checklist item | Value | Unit | Alert limit | Danger limit | Limit direction | Inspector status | Status | Severity | Finding | Recommendation | Priority score | Priority | Due date | Pronto WO no. | Record stage | Inspector | Date closed | Verified by | Days open | Due status | Remarks | Failure mode (ISO 14224) | Failure mechanism (ISO 14224) | Damage mechanism (API 571) | Execution window | Likelihood override (1-5)
R00001 | 2025-10-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00002 | 2025-10-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 12 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00003 | 2025-10-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00004 | 2025-10-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00005 | 2025-10-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00006 | 2025-10-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 150 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00007 | 2025-10-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 210 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00008 | 2025-10-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 3.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00009 | 2025-10-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 240 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00010 | 2025-10-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 10 | ppm | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00011 | 2025-10-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 8 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00012 | 2025-10-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 20 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00013 | 2025-10-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 18 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00014 | 2025-10-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00015 | 2025-10-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00016 | 2025-10-18 | 100114 | Acid transfer line | Acid plant | A | 81 | Ultrasonic report | Ultrasonic thickness | Elbow E-07 wall | 5.6 | mm | 4.5 | 4 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00017 | 2025-10-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 5 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00018 | 2025-10-20 | 100113 | Product acid storage tank | Acid plant | A | 76 | Ultrasonic report | Ultrasonic thickness | Shell course 1 thickness | 8 | mm | 7.5 | 6.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00019 | 2025-10-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00020 | 2025-10-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00021 | 2025-10-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 12 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00022 | 2025-10-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 2 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00023 | 2025-10-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 2 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00024 | 2025-10-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 470 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00025 | 2025-10-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 20 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00026 | 2025-10-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 455 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00027 | 2025-10-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 4.2 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00028 | 2025-10-28 | 100102 | Waste heat boiler | Acid plant | A | 91 | Ultrasonic report | Ultrasonic thickness | Economiser tube minimum wall | 6.2 | mm | 5 | 4.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00029 | 2025-11-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00030 | 2025-11-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 11 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00031 | 2025-11-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00032 | 2025-11-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00033 | 2025-11-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00034 | 2025-11-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 180 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00035 | 2025-11-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 215 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00036 | 2025-11-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 3.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00037 | 2025-11-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 245 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00038 | 2025-11-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 12 | ppm | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00039 | 2025-11-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 9 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00040 | 2025-11-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 22 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00041 | 2025-11-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 19 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00042 | 2025-11-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00043 | 2025-11-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00044 | 2025-11-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 6 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00045 | 2025-11-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00046 | 2025-11-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00047 | 2025-11-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 14 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00048 | 2025-11-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 2 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00049 | 2025-11-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00050 | 2025-11-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 475 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00051 | 2025-11-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 22 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00052 | 2025-11-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 458 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00053 | 2025-11-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 4.2 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00054 | 2025-12-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00055 | 2025-12-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 13 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00056 | 2025-12-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00057 | 2025-12-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00058 | 2025-12-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00059 | 2025-12-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 160 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00060 | 2025-12-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 212 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00061 | 2025-12-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 3.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00062 | 2025-12-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 250 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00063 | 2025-12-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 12 | ppm | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00064 | 2025-12-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 8 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00065 | 2025-12-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 21 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00066 | 2025-12-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 20 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00067 | 2025-12-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00068 | 2025-12-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00069 | 2025-12-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 6 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00070 | 2025-12-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00071 | 2025-12-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00072 | 2025-12-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 15 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00073 | 2025-12-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00074 | 2025-12-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00075 | 2025-12-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 480 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00076 | 2025-12-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 21 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00077 | 2025-12-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 450 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00078 | 2025-12-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 4.1 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00079 | 2026-01-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00080 | 2026-01-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 12 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00081 | 2026-01-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00082 | 2026-01-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00083 | 2026-01-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00084 | 2026-01-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 200 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00085 | 2026-01-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 220 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00086 | 2026-01-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 3.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00087 | 2026-01-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 248 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00088 | 2026-01-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 14 | ppm | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00089 | 2026-01-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 10 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00090 | 2026-01-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 25 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00091 | 2026-01-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 19 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00092 | 2026-01-10 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Alignment condition | [5 empty] | Alert | Alert | 1 | Misalignment signature (2x) at coupling | Laser align pump and motor | 46 | P2 | 2026-02-09 | 242210 | Closed | RCM Specialist | 2026-01-30 | Mechanical Supervisor | 20 | Closed on time
R00093 | 2026-01-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00094 | 2026-01-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00095 | 2026-01-18 | 100114 | Acid transfer line | Acid plant | A | 81 | Ultrasonic report | Ultrasonic thickness | Elbow E-07 wall | 5.4 | mm | 4.5 | 4 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00096 | 2026-01-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 7 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00097 | 2026-01-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00098 | 2026-01-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00099 | 2026-01-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 18 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00100 | 2026-01-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00101 | 2026-01-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 2 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00102 | 2026-01-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 478 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00103 | 2026-01-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 25 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00104 | 2026-01-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 460 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00105 | 2026-01-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 4.1 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00106 | 2026-01-28 | 100102 | Waste heat boiler | Acid plant | A | 91 | Ultrasonic report | Ultrasonic thickness | Economiser tube minimum wall | 6.15 | mm | 5 | 4.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00107 | 2026-02-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00108 | 2026-02-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 12 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00109 | 2026-02-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00110 | 2026-02-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00111 | 2026-02-03 | 100103 | Main air blower | Acid plant | A | 87 | Oil analysis | Lubrication / oil | Oil contamination | [5 empty] | Alert | Alert | 1 | Particle count ISO 21/19/16, above target | Change oil and filters | 52 | P2 | 2026-03-05 | 242530 | Closed | RCM Specialist | 2026-02-25 | Mechanical Supervisor | 22 | Closed on time
R00112 | 2026-02-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00113 | 2026-02-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 240 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00114 | 2026-02-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 230 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00115 | 2026-02-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00116 | 2026-02-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 255 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00117 | 2026-02-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 16 | ppm | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00118 | 2026-02-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 9 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00119 | 2026-02-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 24 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00120 | 2026-02-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 22 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00121 | 2026-02-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00122 | 2026-02-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00123 | 2026-02-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 8 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00124 | 2026-02-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00125 | 2026-02-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00126 | 2026-02-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 22 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00127 | 2026-02-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 5 | °C | 4 | 15 | Higher is worse |  | Alert | 1 | LV connection running warm | Clean and retorque connection | 52 | P2 | 2026-03-26 | 243120 | Closed | Electrician | 2026-04-15 | Electrical Supervisor | 50 | Closed late
R00128 | 2026-02-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00129 | 2026-02-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 485 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00130 | 2026-02-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 24 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00131 | 2026-02-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 462 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00132 | 2026-02-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 4 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00133 | 2026-03-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00134 | 2026-03-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 14 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00135 | 2026-03-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00136 | 2026-03-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00137 | 2026-03-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00138 | 2026-03-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 300 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00139 | 2026-03-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 238 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00140 | 2026-03-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 4.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00141 | 2026-03-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 262 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00142 | 2026-03-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 18 | ppm | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00143 | 2026-03-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 11 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00144 | 2026-03-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 26 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00145 | 2026-03-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 21 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00146 | 2026-03-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00147 | 2026-03-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00148 | 2026-03-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 9 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00149 | 2026-03-20 | 100110 | Molten sulphur pump | Acid plant | B | 61 | IR survey | Infrared | Motor DE bearing temperature | [5 empty] | Alert | Alert | 1 | Motor DE bearing 25 °C above NDE | Replace motor bearing in planned window | 37 | P3 | 2026-05-19 | 242980 | Closed | RCM Specialist | 2026-04-10 | Electrical Supervisor | 21 | Closed on time
R00150 | 2026-03-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00151 | 2026-03-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00152 | 2026-03-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 30 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00153 | 2026-03-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 6 | °C | 4 | 15 | Higher is worse |  | Alert | 1 |  |  | 52 | P2 | 2026-04-23 |  | No action | Electrician |  |  | 195 | Overdue
R00154 | 2026-03-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00155 | 2026-03-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 490 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00156 | 2026-03-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 23 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00157 | 2026-03-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 458 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00158 | 2026-03-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 4 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00159 | 2026-04-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00160 | 2026-04-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 13 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00161 | 2026-04-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00162 | 2026-04-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00163 | 2026-04-02 | 100113 | Product acid storage tank | Acid plant | A | 76 | Ultrasonic report | Ultrasonic thickness | Shell course 1 thickness | 7.4 | mm | 7.5 | 6.5 | Lower is worse |  | Alert | 1 | Shell at 74% of nominal 10 mm | Fitness-for-service assessment; UT quarterly | 46 | P2 | 2026-05-02 |  | Raised | UT contractor |  |  | 186 | Overdue
R00164 | 2026-04-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00165 | 2026-04-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 420 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00166 | 2026-04-05 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | Oil analysis | Lubrication / oil | Girth gear lubricant | [5 empty] | Alert | Alert | 1 | Girth gear lubricant degraded, high iron | Clean gear and reapply lubricant | 54 | P2 | 2026-05-05 | 243305 | Closed | RCM Specialist | 2026-05-20 | Mechanical Supervisor | 45 | Closed late
R00167 | 2026-04-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 245 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00168 | 2026-04-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 4.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00169 | 2026-04-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 268 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00170 | 2026-04-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 22 | ppm | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00171 | 2026-04-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 10 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00172 | 2026-04-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 28 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00173 | 2026-04-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 23 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00174 | 2026-04-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00175 | 2026-04-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00176 | 2026-04-18 | 100114 | Acid transfer line | Acid plant | A | 81 | Ultrasonic report | Ultrasonic thickness | Elbow E-07 wall | 5.1 | mm | 4.5 | 4 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00177 | 2026-04-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 10 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00178 | 2026-04-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00179 | 2026-04-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00180 | 2026-04-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 8 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00181 | 2026-04-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 2 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00182 | 2026-04-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00183 | 2026-04-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 495 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00184 | 2026-04-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 26 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00185 | 2026-04-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 465 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00186 | 2026-04-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 3.9 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00187 | 2026-04-28 | 100102 | Waste heat boiler | Acid plant | A | 91 | Ultrasonic report | Ultrasonic thickness | Economiser tube minimum wall | 6.11 | mm | 5 | 4.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00188 | 2026-05-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00189 | 2026-05-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 12 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00190 | 2026-05-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00191 | 2026-05-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00192 | 2026-05-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00193 | 2026-05-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 550 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00194 | 2026-05-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 248 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00195 | 2026-05-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 4.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 | Gear-mesh sidebands rising | Borescope gearbox; plan overhaul and order spare | 30 | P3 | 2026-07-09 | 243766 | Scheduled | RCM Specialist |  |  | 148 | Overdue
R00196 | 2026-05-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 270 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00197 | 2026-05-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 32 | ppm | 30 | 60 | Higher is worse |  | Alert | 1 | Copper wear metal rising | Oil change; trend wear metals monthly | 30 | P3 | 2026-07-09 | 243767 | Scheduled | RCM Specialist |  |  | 148 | Overdue
R00198 | 2026-05-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 12 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00199 | 2026-05-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 27 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00200 | 2026-05-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 22 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00201 | 2026-05-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00202 | 2026-05-12 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Ultrasonic report | Ultrasonics (airborne) | NDE bearing lubrication | [5 empty] | Alert | Alert | 1 | NDE bearing under-lubricated (ultrasound +8 dB) | Regrease by ultrasound | 43 | P3 | 2026-07-11 | 243620 | Closed | RCM Specialist | 2026-06-02 | Mechanical Supervisor | 21 | Closed on time
R00203 | 2026-05-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00204 | 2026-05-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 12 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00205 | 2026-05-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00206 | 2026-05-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00207 | 2026-05-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 10 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00208 | 2026-05-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00209 | 2026-05-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 16 | °C | 4 | 15 | Higher is worse |  | Danger | 2 | Feeder F-03 termination loose | Re-terminate lug | 82 | P1 | 2026-05-31 | 243910 | Closed | RCM Specialist | 2026-05-29 | Electrical Supervisor | 5 | Closed on time
R00210 | 2026-05-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 500 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00211 | 2026-05-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 25 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00212 | 2026-05-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 460 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00213 | 2026-05-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 3.9 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00214 | 2026-06-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00215 | 2026-06-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 32 | dBµV | 30 | 40 | Higher is worse |  | Alert | 1 | Drain valve passing air | Replace drain valve | 32 | P3 | 2026-07-31 | 243955 | Closed | RCM Specialist | 2026-06-20 | Mechanical Supervisor | 19 | Closed on time
R00216 | 2026-06-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00217 | 2026-06-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00218 | 2026-06-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00219 | 2026-06-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 700 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00220 | 2026-06-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 250 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00221 | 2026-06-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 5.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-08-09 |  | No action | RCM Specialist |  |  | 117 | Overdue
R00222 | 2026-06-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 272 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00223 | 2026-06-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 34 | ppm | 30 | 60 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-08-09 |  | No action | RCM Specialist |  |  | 117 | Overdue
R00224 | 2026-06-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 14 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00225 | 2026-06-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 30 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00226 | 2026-06-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 24 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00227 | 2026-06-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.5 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00228 | 2026-06-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 | Looseness pattern at pump feet | Check holding-down bolts and soft foot | 40 | P3 | 2026-08-14 |  | Raised | RCM Specialist |  |  | 112 | Overdue
R00229 | 2026-06-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 22 | °C | 30 | 60 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00230 | 2026-06-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00231 | 2026-06-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00232 | 2026-06-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 12 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00233 | 2026-06-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00234 | 2026-06-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00235 | 2026-06-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 505 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00236 | 2026-06-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 27 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00237 | 2026-06-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 463 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00238 | 2026-06-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 3.8 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00239 | 2026-07-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00240 | 2026-07-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 12 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00241 | 2026-07-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 | Looseness at pump base | Retorque base bolts | 45 | P2 | 2026-08-01 | 244402 | Closed | RCM Specialist | 2026-08-12 | Mechanical Supervisor | 41 | Closed late
R00242 | 2026-07-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00243 | 2026-07-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00244 | 2026-07-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 850 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00245 | 2026-07-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 265 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00246 | 2026-07-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 5.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-09-08 |  | No action | RCM Specialist |  |  | 87 | Overdue
R00247 | 2026-07-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 276 | °C | 280 | 350 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00248 | 2026-07-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 36 | ppm | 30 | 60 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-09-08 |  | No action | RCM Specialist |  |  | 87 | Overdue
R00249 | 2026-07-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 16 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00250 | 2026-07-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 29 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00251 | 2026-07-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 23 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00252 | 2026-07-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00253 | 2026-07-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 |  |  | 40 | P3 | 2026-09-13 |  | No action | RCM Specialist |  |  | 82 | Overdue
R00254 | 2026-07-15 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Oil analysis | Lubrication / oil | Particle count | [5 empty] | Alert | Alert | 1 | High particle count in gearbox oil | Flush oil and replace breather | 26 | P3 | 2026-09-13 | 244150 | Closed | RCM Specialist | 2026-08-30 | Mechanical Supervisor | 46 | Closed on time
R00255 | 2026-07-18 | 100114 | Acid transfer line | Acid plant | A | 81 | Ultrasonic report | Ultrasonic thickness | Elbow E-07 wall | 4.7 | mm | 4.5 | 4 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00256 | 2026-07-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 31 | °C | 30 | 60 | Higher is worse |  | Alert | 1 | Bed 3 outlet flange running hot | Hot-retorque flange bolts; check gasket | 52 | P2 | 2026-08-19 | 244512 | Scheduled | RCM Specialist |  |  | 77 | Overdue
R00257 | 2026-07-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 3.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00258 | 2026-07-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00259 | 2026-07-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 16 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00260 | 2026-07-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | Electrician
R00261 | 2026-07-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00262 | 2026-07-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 510 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00263 | 2026-07-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 30 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00264 | 2026-07-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 466 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00265 | 2026-07-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 3.7 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00266 | 2026-08-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00267 | 2026-08-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 14 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00268 | 2026-08-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00269 | 2026-08-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00270 | 2026-08-03 | 100101 | Sulphur furnace | Acid plant | A | 94 | Vibration & visual route | Structural | Burner platform support | [5 empty] | Alert | Alert | 1 | Crack at support bracket weld | Repair weld; MPI after repair | 56 | P2 | 2026-09-02 | 244380 | Closed | RCM Specialist | 2026-08-28 | Mechanical Supervisor | 25 | Closed on time
R00271 | 2026-08-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00272 | 2026-08-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 980 | ppm | 1000 | 2000 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00273 | 2026-08-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 278 | °C | 280 | 320 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00274 | 2026-08-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 6.4 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-10-09 |  | No action | RCM Specialist |  |  | 56 | Within time
R00275 | 2026-08-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 282 | °C | 280 | 350 | Higher is worse |  | Alert | 1 | Zone 4 shell hot spot, rising | Check refractory; run shell cooling fan | 54 | P2 | 2026-09-09 |  | Raised | RCM Specialist |  |  | 56 | Overdue
R00276 | 2026-08-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 38 | ppm | 30 | 60 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-10-09 |  | No action | RCM Specialist |  |  | 56 | Within time
R00277 | 2026-08-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 18 | ppm | 20 | 30 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00278 | 2026-08-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 31 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00279 | 2026-08-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 25 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00280 | 2026-08-11 | 100502 | Light vehicle LV-02 (pickup) | Mobile fleet | C | 41 | LV/HV prestart checklist | Prestart | Seatbelt | [5 empty] | Danger | Danger | 2 | Driver seatbelt not latching; vehicle tagged out | Replace seatbelt buckle | 41 | P1 | 2026-08-18 | 244620 | Closed | Operator | 2026-08-12 | Fleet Supervisor | 1 | Closed on time
R00281 | 2026-08-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00282 | 2026-08-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.9 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 |  |  | 40 | P3 | 2026-10-14 |  | No action | RCM Specialist |  |  | 51 | Within time
R00283 | 2026-08-18 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Oil analysis | Lubrication / oil | Oil oxidation | [5 empty] | Alert | Alert | 1 | Oxidation above limit | Change oil | 46 | P2 | 2026-09-17 | 244690 | Closed | RCM Specialist | 2026-09-10 | Mechanical Supervisor | 23 | Closed on time
R00284 | 2026-08-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 38 | °C | 30 | 60 | Higher is worse |  | Alert | 1 |  |  | 52 | P2 | 2026-09-19 |  | No action | RCM Specialist |  |  | 46 | Overdue
R00285 | 2026-08-20 | 100104 | SO2 converter | Acid plant | A | 86 | Vibration & visual route | Tank & vessel | Manway gasket | [5 empty] | Alert | Alert | 1 | Manway gasket weeping | Replace gasket at opportunity | 52 | P2 | 2026-09-19 | 244720 | Closed | RCM Specialist | 2026-09-25 | Mechanical Supervisor | 36 | Closed late
R00286 | 2026-08-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00287 | 2026-08-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.3 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00288 | 2026-08-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 24 | ppm | 50 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00289 | 2026-08-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 12 | °C | 4 | 15 | Higher is worse |  | Alert | 1 | LV bushing connection hot, rising | Clean and retorque at next outage | 52 | P2 | 2026-09-23 | 244871 | WO raised | Electrician |  |  | 42 | Overdue
R00290 | 2026-08-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 3 | °C | 4 | 15 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00291 | 2026-08-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 515 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00292 | 2026-08-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 32 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00293 | 2026-08-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 462 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00294 | 2026-08-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 3.6 | bar | 3.5 | 2.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00295 | 2026-08-28 | 100102 | Waste heat boiler | Acid plant | A | 91 | Ultrasonic report | Ultrasonic thickness | Economiser tube minimum wall | 6.05 | mm | 5 | 4.5 | Lower is worse |  | OK | 0 | [6 empty] | No action | UT contractor
R00296 | 2026-09-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00297 | 2026-09-01 | 100115 | Instrument air receiver | Acid plant | B | 53 | Ultrasonic report | Ultrasonics (airborne) | Leak survey level | 13 | dBµV | 30 | 40 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00298 | 2026-09-01 | 100102 | Waste heat boiler | Acid plant | A | 91 | Statutory inspection | Statutory | Pressure vessel certificate | [5 empty] | Alert | Alert | 1 | Certificate expires 22 Oct 2026; inspection not booked | Book statutory inspector; prepare hydro test | 55 | P2 | 2026-10-01 | 244930 | Scheduled | RCM Specialist |  |  | 34 | Overdue
R00299 | 2026-09-01 | 100110 | Molten sulphur pump | Acid plant | B | 61 | Vibration & visual route | Vibration | Coupling condition | [5 empty] | Alert | Alert | 1 | Coupling element wear indicated | Replace coupling element | 37 | P3 | 2026-10-31 | 244950 | Closed | RCM Specialist | 2026-09-14 | Mechanical Supervisor | 13 | Closed on time
R00300 | 2026-09-02 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.7 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00301 | 2026-09-02 | 100111 | Sulphur melter agitator | Acid plant | C | 43 | Vibration & visual route | Vibration | Overall velocity (max point) | 1.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00302 | 2026-09-05 | 100109 | Boiler feed water pump B | Acid plant | A | 71 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.1 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00303 | 2026-09-05 | 100108 | Boiler feed water pump A | Acid plant | A | 75 | Oil analysis | Lubrication / oil | Water in bearing oil | 1200 | ppm | 1000 | 2000 | Higher is worse |  | Alert | 1 | Water contamination in bearing oil | Change oil; fit desiccant breather; check seal | 45 | P2 | 2026-10-05 | 245044 | WO raised | RCM Specialist |  |  | 30 | Within time
R00304 | 2026-09-08 | 100101 | Sulphur furnace | Acid plant | A | 94 | IR survey | Infrared | Burner-end shell temperature | 340 | °C | 280 | 320 | Higher is worse |  | Danger | 2 | Burner-end shell hot spot: refractory loss suspected | Refractory inspection at next stop; daily IR until then | 94 | P1 | 2026-09-15 | 245011 | Scheduled | RCM Specialist |  |  | 27 | Overdue
R00305 | 2026-09-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Vibration & visual route | Vibration | Gearbox overall velocity | 6.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-11-09 |  | No action | RCM Specialist |  |  | 25 | Within time
R00306 | 2026-09-10 | 100201 | Calciner kiln 1080 | Calciner | A | 90 | IR survey | Infrared | Zone 4 shell temperature | 310 | °C | 280 | 350 | Higher is worse |  | Alert | 1 |  |  | 54 | P2 | 2026-10-10 |  | No action | RCM Specialist |  |  | 25 | Within time
R00307 | 2026-09-10 | 100112 | Cooling tower fan 1 | Acid plant | B | 50 | Oil analysis | Lubrication / oil | Copper (Cu) in gearbox oil | 40 | ppm | 30 | 60 | Higher is worse |  | Alert | 1 |  |  | 30 | P3 | 2026-11-09 |  | No action | RCM Specialist |  |  | 25 | Within time
R00308 | 2026-09-10 | 100603 | Front-end loader HV-03 | Mobile fleet | B | 67 | Oil analysis | Lubrication / oil | Engine oil silicon (Si) | 22 | ppm | 20 | 30 | Higher is worse |  | Alert | 1 | Silicon elevated: dirt entry via air intake suspected | Inspect intake hoses and filter seals; resample | 40 | P3 | 2026-11-09 |  | Raised | RCM Specialist |  |  | 25 | Within time
R00309 | 2026-09-10 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 33 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00310 | 2026-09-10 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | Oil analysis | Lubrication / oil | Engine oil iron (Fe) | 24 | ppm | 60 | 100 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00311 | 2026-09-12 | 100103 | Main air blower | Acid plant | A | 87 | Vibration & visual route | Vibration | Overall velocity (max point) | 4.6 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 | 1x running speed rising: unbalance | Clean impeller; trim balance at next stop | 52 | P2 | 2026-10-12 | 245102 | WO raised | RCM Specialist |  |  | 23 | Within time
R00312 | 2026-09-15 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Vibration | Overall velocity (max point) | 5.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | Alert | 1 |  |  | 40 | P3 | 2026-11-14 |  | No action | RCM Specialist |  |  | 20 | Within time
R00313 | 2026-09-15 | 100601 | Dozer HV-01 | Mobile fleet | B | 69 | LV/HV inspection checklist | Fleet inspection | Undercarriage: track link wear | [5 empty] | Alert | Alert | 1 | Track links approx. 70% worn | Plan undercarriage replacement; order parts | 41 | P3 | 2026-11-14 |  | Raised | Fleet mechanic |  |  | 20 | Within time
R00314 | 2026-09-16 | 100107 | Final tower acid pump | Acid plant | B | 66 | Vibration & visual route | Visual | Holding-down bolts | [5 empty] | Alert | Alert | 1 | Two holding-down bolts loose on pump base | Retorque bolts; check soft foot | 40 | P3 | 2026-11-15 |  | Raised | RCM Specialist |  |  | 19 | Within time
R00315 | 2026-09-18 | 100114 | Acid transfer line | Acid plant | A | 81 | Ultrasonic report | Ultrasonic thickness | Elbow E-07 wall | 3.9 | mm | 4.5 | 4 | Lower is worse |  | Danger | 2 | Wall below 4.0 mm minimum required | Replace elbow spool; extend UT grid +/-1 m | 81 | P1 | 2026-09-25 | 245207 | Scheduled | UT contractor |  |  | 17 | Overdue
R00316 | 2026-09-20 | 100104 | SO2 converter | Acid plant | A | 86 | IR survey | Infrared | Bed 3 outlet flange dT above baseline | 45 | °C | 30 | 60 | Higher is worse |  | Alert | 1 |  |  | 52 | P2 | 2026-10-20 |  | No action | RCM Specialist |  |  | 15 | Within time
R00317 | 2026-09-20 | 100113 | Product acid storage tank | Acid plant | A | 76 | Ultrasonic report | Ultrasonic thickness | Shell course 1 thickness | 7.2 | mm | 7.5 | 6.5 | Lower is worse |  | Alert | 1 |  |  | 46 | P2 | 2026-10-20 |  | No action | UT contractor |  |  | 15 | Within time
R00318 | 2026-09-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Vibration & visual route | Vibration | Overall velocity (max point) | 9.8 | mm/s | 4.5 | 7.1 | Higher is worse |  | Danger | 2 | DE bearing outer race defect (BPFO) with harmonics | Replace DE bearing; check alignment and soft foot | 74 | P1 | 2026-09-29 | 245289 | WO raised | RCM Specialist |  |  | 13 | Overdue
R00319 | 2026-09-22 | 100106 | Interpass tower acid pump | Acid plant | A | 76 | Vibration & visual route | Vibration | Overall velocity (max point) | 2.2 | mm/s | 4.5 | 7.1 | Higher is worse |  | OK | 0 | [6 empty] | No action | RCM Specialist
R00320 | 2026-09-22 | 100105 | Drying tower acid pump | Acid plant | A | 74 | Oil analysis | Lubrication / oil | Iron (Fe) | 85 | ppm | 50 | 100 | Higher is worse |  | Alert | 1 | Iron rising sharply, oil darkened | Oil change and filter; resample in 2 weeks | 44 | P3 | 2026-11-21 | 245290 | Awaiting verification | RCM Specialist |  |  | 13 | Within time
R00321 | 2026-09-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Infrared | LV bushing connection dT | 14 | °C | 4 | 15 | Higher is worse |  | Alert | 1 |  |  | 52 | P2 | 2026-10-24 |  | No action | Electrician |  |  | 11 | Within time
R00322 | 2026-09-24 | 100302 | Acid plant MCC | Substation | A | 82 | IR survey | Infrared | Hottest termination dT | 42 | °C | 4 | 15 | Higher is worse |  | Danger | 2 | B-phase breaker termination 42 °C above A and C | Isolate, re-terminate and torque lugs; re-scan | 82 | P1 | 2026-10-01 | 245318 | WO raised | RCM Specialist |  |  | 11 | Overdue
R00323 | 2026-09-24 | 100301 | Transformer TX-01 | Substation | A | 86 | Substation inspection | Visual | Silica gel breather | [5 empty] | Alert | Alert | 1 | More than two-thirds of silica gel discoloured | Replace silica gel | 52 | P2 | 2026-10-24 |  | Raised | Electrician |  |  | 11 | Within time
R00324 | 2026-09-24 | 100302 | Acid plant MCC | Substation | A | 82 | Substation inspection | Electrical | Feeder F-12 insulation resistance | 12 | MΩ | 100 | 10 | Lower is worse |  | Alert | 1 | Insulation resistance low on F-12 | Dry out and retest cable; PI test | 49 | P2 | 2026-10-24 |  | Raised | Electrician |  |  | 11 | Within time
R00325 | 2026-09-28 | 100401 | Diesel generator Gen 1 | Power plant | A | 83 | DG checklist | DG checks | Turbo outlet exhaust temperature | 560 | °C | 520 | 580 | Higher is worse |  | Alert | 1 | Turbo outlet temperature above alert, rising over 3 days | Check air filter, intercooler and injector balance | 50 | P2 | 2026-10-28 |  | Raised | DG operator |  |  | 7 | Within time
R00326 | 2026-09-28 | 100402 | Diesel generator Gen 2 | Power plant | A | 79 | DG checklist | DG checks | Exhaust temperature spread between cylinders | 35 | °C | 50 | 80 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00327 | 2026-09-28 | 100403 | Diesel generator Gen 3 | Power plant | A | 79 | DG checklist | DG checks | Turbo outlet exhaust temperature | 465 | °C | 520 | 580 | Higher is worse |  | OK | 0 | [6 empty] | No action | DG operator
R00328 | 2026-09-28 | 100404 | Diesel generator Gen 4 | Power plant | A | 92 | DG checklist | DG checks | Lube oil pressure at rated load | 3.1 | bar | 3.5 | 2.5 | Lower is worse |  | Alert | 1 | Oil pressure below alert at rated load | Check oil level, filter differential and pump | 55 | P2 | 2026-10-28 |  | Raised | DG operator |  |  | 7 | Within time
R00329 | 2026-09-29 | 100602 | Compactor HV-02 | Mobile fleet | B | 58 | LV/HV prestart checklist | Prestart | Service brake | [5 empty] | Danger | Danger | 2 | Brake ineffective; machine tagged out | Repair brakes before operation; verify by mechanic | 58 | P1 | 2026-10-06 | 245402 | WO raised | Operator |  |  | 6 | Within time
R00330 | 2026-09-29 | 100501 | Light vehicle LV-01 (pickup) | Mobile fleet | C | 43 | LV/HV prestart checklist | Prestart | Reverse alarm | [5 empty] | Alert | Alert | 1 | Reverse alarm not working | Replace reverse alarm | 26 | P3 | 2026-11-28 |  | Raised | Operator |  |  | 6 | Within time
Formulas:
Days open = IF(OR([Priority score]="",[Date]=""),"",IF([Date closed]<>"",[Date closed]-[Date],TODAY()-[Date]))
Due status = IF([Due date]="","",IF([Record stage]="Closed",IF([Date closed]="","Closed",IF([Date closed]<=[Due date],"Closed on time","Closed late")),IF(TODAY()>[Due date],"Overdue","Within time")))
Due date = IF(OR([Priority]="",[Date]=""),"",[Date]+INDEX(Lists!$N10:N12,MATCH([Priority],Lists!$L10:L12,0)))
Note on P4: Checklists / visual / statutory: choose OK, Alert or Danger using the severity rules in the Guide. Measured values: leave blank and status is calculated from the limits; fill only to override (analyst judgement).
Note on Y4: OK records: No action. Alert/Danger: Raised -> WO raised -> Scheduled -> Awaiting verification -> Closed. Close only after a re-check confirms the fix.

## Lists
Areas | Asset classes | Sources (input) | Techniques | Record stages | Status | Limit direction | Asset state | Operating mode | Yes / No | ACI factor | Weight
Acid plant | Rotating - pump | Vibration & visual route | Vibration | No action | OK | Higher is worse | Active | Duty | Y | Safety & environment | 0.3
Calciner | Rotating - fan / blower | IR survey | Lubrication / oil | Raised | Alert | Lower is worse | Standby | Standby | N | Production impact | 0.3
Substation | Rotating - gearbox / drive | Substation inspection | Ultrasonics (airborne) | WO raised | Danger |  | Out of service | Mobile |  | Redundancy | 0.15
Power plant | Rotating - agitator | Statutory inspection | Ultrasonic thickness | Scheduled |  |  | Decommissioned |  |  | Repair cost / MTTR | 0.15
Mobile fleet | Rotary kiln | Ultrasonic report | Infrared | Awaiting verification | [5 empty] | Failure history | 0.1
Utilities | Fired equipment | Oil analysis | Visual | Closed | [5 empty] | Weights must total 1.00. Agree with Engineering Manager.
| Boiler | DG checklist | Statutory
| Pressure vessel | LV/HV inspection checklist | Tank & vessel | [6 empty] | Priority | Minimum score | Response time (days)
| Tank | LV/HV prestart checklist | Piping | [6 empty] | P1 | 70 | 7
| Piping | Ad hoc / operator report | Structural | [6 empty] | P2 | 45 | 30
| Structure |  | Electrical | [6 empty] | P3 | 0 | 60
| Electrical - transformer |  | DG checks
| Electrical - switchgear / MCC |  | Fleet inspection | [6 empty] | Severity | Factor
| Diesel generator |  | Prestart | [6 empty] | Danger | 1
| Light vehicle | [8 empty] | Alert | 0.6
| Heavy equipment | [8 empty] | Priority score = ACI x severity factor. Any Danger is always P1.
[10 empty] | Criticality class | Minimum ACI
[10 empty] | A | 70
[10 empty] | B | 45
[10 empty] | C | 0
[10 empty] | Statutory rule | Days
[10 empty] | Expiry alert window | 60
Certificate expiring within this window = Alert; expired = Danger
[10 empty] | Condition score (for AHI) | Score
[10 empty] | OK | 100
[10 empty] | Alert | 60
[10 empty] | Danger | 20
[10 empty] | Unknown | 50
Unknown = not inspected within the required interval
[10 empty] | KPI target | Value
[10 empty] | Asset Health Index | 85
[10 empty] | Inspection schedule compliance % | 95
[10 empty] | Recommendations closed on time % | 85
[10 empty] | Overdue recommendations (max) | 2
[10 empty] | CM return on investment (x : 1) | 4
[10 empty] | Critical asset CM coverage % | 90
[10 empty] | Prestart compliance % | 95
Targets shown on the Management page. Approve with the Engineering Manager.
[10 empty] | Inspection interval | Days
[10 empty] | A | 30
[10 empty] | B | 60
[10 empty] | C | 90
Maximum days between inspections by criticality class. Older = Unknown.
Blue text on cream = settings you can change. Every formula in the workbook reads from these cells.

## Events
AHIM Event History (from Pronto)
One row per failure, repair, PM or shutdown from Pronto work orders. Downtime only on Failure rows. Used for MTBF, MTTR, availability and bad actors.
Date | Pronto asset no. | Event type | Description | Downtime (h) | Pronto WO no. | RCA reference
2025-11-14 | 100103 | PM | Annual service: coupling, filters, inlet guide vanes | 0 | 241050
2025-11-30 | 100110 | Failure | Steam jacket leak, pump stopped | 5 | 241210
2025-12-01 | 100110 | Repair | Jacket gasket replaced | 0 | 241210
2025-12-05 | 100404 | Failure | Fuel injector failure, unit offline | 10 | 241260 | RCA-2025-07
2025-12-06 | 100404 | Repair | Injector replaced, load test passed | 0 | 241260
2025-12-10 | 100105 | Failure | Mechanical seal leak | 8 | 241300
2025-12-10 | 100105 | Repair | Seal replaced | 0 | 241300
2025-12-15 | 100201 | Failure | Girth gear lubrication spray failure | 18 | 241350
2025-12-16 | 100201 | Repair | Spray nozzles replaced | 0 | 241350
2026-01-08 | 100112 | Failure | Fan blade pitch slipped, high vibration trip | 4 | 242100
2026-01-08 | 100112 | Repair | Blades re-pitched and balanced | 0 | 242100
2026-01-12 | 100107 | Failure | Impeller wear, low discharge pressure | 10 | 242150
2026-01-13 | 100107 | Repair | Impeller replaced | 0 | 242150
2026-01-20 | 100103 | Failure | Inlet guide vane actuator seized, blower tripped | 6 | 242300
2026-01-20 | 100103 | Repair | Actuator replaced and calibrated | 0 | 242300
2026-02-10 | 100601 | Failure | Hydraulic hose burst | 6 | 242400
2026-02-14 | 100102 | Failure | Economiser tube leak, plant stopped | 36 | 242450 | RCA-2026-02
2026-02-16 | 100102 | Repair | Two tubes plugged, hydro test passed | 0 | 242450
2026-02-14 | 100104 | PM | Catalyst screening bed 1 during shutdown | 0 | 242460
2026-02-20 | 100302 | Failure | Feeder F-07 contactor burned, trip | 3 | 242600
2026-02-20 | 100302 | Repair | Contactor replaced | 0 | 242600
2026-03-11 | 100401 | Failure | Turbocharger oil feed line leak, unit stopped | 20 | 242800 | RCA-2026-03
2026-03-12 | 100401 | Repair | Oil feed line and clamps replaced | 0 | 242800
2026-04-20 | 100201 | PM | Tyre and roller alignment check | 0 | 243200
2026-04-22 | 100105 | Failure | DE bearing failure | 14 | 243250 | RCA-2026-04
2026-04-23 | 100105 | Repair | Bearings replaced; alignment 0.08 mm | 0 | 243250
2026-05-14 | 100301 | PM | Annual electrical maintenance | 0 | 243500
2026-06-18 | 100404 | Failure | Coolant hose burst, high temperature trip | 8 | 243900
2026-06-18 | 100404 | Repair | Coolant hoses replaced | 0 | 243900
2026-07-05 | 100114 | Failure | Pinhole leak at elbow E-04, line isolated | 12 | 244200
2026-07-06 | 100114 | Repair | Elbow E-04 replaced | 0 | 244200
2026-07-22 | 100602 | Failure | Alternator failure | 5 | 244300

## Schedule
AHIM Inspection Schedule Compliance
One row per month and technique: inspections planned vs completed (from the CM schedule / Pronto PM routes).
Month | Technique | Planned | Completed
2025-10-01 | Vibration | 42 | 42
2025-10-01 | Lubrication / oil | 34 | 33
2025-10-01 | Ultrasonics (airborne) | 18 | 18
2025-10-01 | Ultrasonic thickness | 6 | 4
2025-10-01 | Infrared | 24 | 23
2025-10-01 | Visual | 40 | 40
2025-10-01 | Statutory | 1 | 1
2025-10-01 | Tank & vessel | 1 | 0
2025-10-01 | Piping | 2 | 2
2025-10-01 | Structural | 5 | 5
2025-10-01 | Electrical | 20 | 18
2025-10-01 | DG checks | 120 | 119
2025-10-01 | Fleet inspection | 10 | 10
2025-11-01 | Vibration | 42 | 41
2025-11-01 | Lubrication / oil | 34 | 34
2025-11-01 | Ultrasonics (airborne) | 18 | 16
2025-11-01 | Infrared | 24 | 24
2025-11-01 | Visual | 40 | 39
2025-11-01 | Tank & vessel | 1 | 1
2025-11-01 | Piping | 2 | 2
2025-11-01 | Structural | 5 | 5
2025-11-01 | Electrical | 20 | 19
2025-11-01 | DG checks | 120 | 120
2025-11-01 | Fleet inspection | 10 | 9
2025-12-01 | Vibration | 42 | 42
2025-12-01 | Lubrication / oil | 34 | 32
2025-12-01 | Ultrasonics (airborne) | 18 | 17
2025-12-01 | Infrared | 24 | 23
2025-12-01 | Visual | 40 | 37
2025-12-01 | Tank & vessel | 1 | 1
2025-12-01 | Piping | 2 | 2
2025-12-01 | Structural | 5 | 5
2025-12-01 | Electrical | 20 | 20
2025-12-01 | DG checks | 120 | 119
2025-12-01 | Fleet inspection | 10 | 10
2026-01-01 | Vibration | 42 | 40
2026-01-01 | Lubrication / oil | 34 | 33
2026-01-01 | Ultrasonics (airborne) | 18 | 18
2026-01-01 | Ultrasonic thickness | 6 | 5
2026-01-01 | Infrared | 24 | 21
2026-01-01 | Visual | 40 | 39
2026-01-01 | Tank & vessel | 1 | 1
2026-01-01 | Piping | 2 | 2
2026-01-01 | Structural | 5 | 5
2026-01-01 | Electrical | 20 | 19
2026-01-01 | DG checks | 120 | 120
2026-01-01 | Fleet inspection | 10 | 8
2026-02-01 | Vibration | 42 | 41
2026-02-01 | Lubrication / oil | 34 | 34
2026-02-01 | Ultrasonics (airborne) | 18 | 17
2026-02-01 | Infrared | 24 | 23
2026-02-01 | Visual | 40 | 40
2026-02-01 | Tank & vessel | 1 | 1
2026-02-01 | Piping | 2 | 2
2026-02-01 | Structural | 5 | 5
2026-02-01 | Electrical | 20 | 20
2026-02-01 | DG checks | 120 | 118
2026-02-01 | Fleet inspection | 10 | 9
2026-03-01 | Vibration | 42 | 42
2026-03-01 | Lubrication / oil | 34 | 33
2026-03-01 | Ultrasonics (airborne) | 18 | 15
2026-03-01 | Infrared | 24 | 24
2026-03-01 | Visual | 40 | 38
2026-03-01 | Statutory | 1 | 1
2026-03-01 | Tank & vessel | 1 | 1
2026-03-01 | Piping | 2 | 2
2026-03-01 | Structural | 5 | 4
2026-03-01 | Electrical | 20 | 18
2026-03-01 | DG checks | 120 | 119
2026-03-01 | Fleet inspection | 10 | 10
2026-04-01 | Vibration | 42 | 41
2026-04-01 | Lubrication / oil | 34 | 31
2026-04-01 | Ultrasonics (airborne) | 18 | 17
2026-04-01 | Ultrasonic thickness | 6 | 6
2026-04-01 | Infrared | 24 | 22
2026-04-01 | Visual | 40 | 39
2026-04-01 | Tank & vessel | 1 | 1
2026-04-01 | Piping | 2 | 1
2026-04-01 | Structural | 5 | 5
2026-04-01 | Electrical | 20 | 19
2026-04-01 | DG checks | 120 | 120
2026-04-01 | Fleet inspection | 10 | 9
2026-05-01 | Vibration | 42 | 39
2026-05-01 | Lubrication / oil | 34 | 33
2026-05-01 | Ultrasonics (airborne) | 18 | 18
2026-05-01 | Infrared | 24 | 23
2026-05-01 | Visual | 40 | 40
2026-05-01 | Tank & vessel | 1 | 0
2026-05-01 | Piping | 2 | 2
2026-05-01 | Structural | 5 | 5
2026-05-01 | Electrical | 20 | 20
2026-05-01 | DG checks | 120 | 119
2026-05-01 | Fleet inspection | 10 | 7
2026-06-01 | Vibration | 42 | 41
2026-06-01 | Lubrication / oil | 34 | 34
2026-06-01 | Ultrasonics (airborne) | 18 | 16
2026-06-01 | Infrared | 24 | 24
2026-06-01 | Visual | 40 | 39
2026-06-01 | Tank & vessel | 1 | 1
2026-06-01 | Piping | 2 | 2
2026-06-01 | Structural | 5 | 5
2026-06-01 | Electrical | 20 | 19
2026-06-01 | DG checks | 120 | 117
2026-06-01 | Fleet inspection | 10 | 9
2026-07-01 | Vibration | 42 | 42
2026-07-01 | Lubrication / oil | 34 | 32
2026-07-01 | Ultrasonics (airborne) | 18 | 17
2026-07-01 | Ultrasonic thickness | 6 | 6
2026-07-01 | Infrared | 24 | 23
2026-07-01 | Visual | 40 | 40
2026-07-01 | Tank & vessel | 1 | 1
2026-07-01 | Piping | 2 | 2
2026-07-01 | Structural | 5 | 5
2026-07-01 | Electrical | 20 | 17
2026-07-01 | DG checks | 120 | 119
2026-07-01 | Fleet inspection | 10 | 10
2026-08-01 | Vibration | 42 | 40
2026-08-01 | Lubrication / oil | 34 | 33
2026-08-01 | Ultrasonics (airborne) | 18 | 18
2026-08-01 | Ultrasonic thickness | 6 | 5
2026-08-01 | Infrared | 24 | 24
2026-08-01 | Visual | 40 | 38
2026-08-01 | Tank & vessel | 1 | 1
2026-08-01 | Piping | 2 | 2
2026-08-01 | Structural | 5 | 5
2026-08-01 | Electrical | 20 | 19
2026-08-01 | DG checks | 120 | 120
2026-08-01 | Fleet inspection | 10 | 8
2026-09-01 | Vibration | 42 | 40
2026-09-01 | Lubrication / oil | 34 | 34
2026-09-01 | Ultrasonics (airborne) | 18 | 15
2026-09-01 | Ultrasonic thickness | 6 | 6
2026-09-01 | Infrared | 24 | 24
2026-09-01 | Visual | 40 | 40
2026-09-01 | Statutory | 1 | 0
2026-09-01 | Tank & vessel | 1 | 1
2026-09-01 | Piping | 2 | 2
2026-09-01 | Structural | 5 | 3
2026-09-01 | Electrical | 20 | 18
2026-09-01 | DG checks | 120 | 116
2026-09-01 | Fleet inspection | 10 | 9

## CM_Value
AHIM Condition Monitoring Value (cost avoidance)
Net avoided = avoided failure cost (repair + collateral damage + lost production) minus planned repair cost. Count only when approved.
Date | Pronto asset no. | Technique | Detection / failure avoided | Avoided failure cost (USD) | Planned repair cost (USD) | Approved by
2025-11-20 | 100109 | Vibration | Bearing defect found early; replaced in planned window | 22000 | 2500 | Engineering Manager
2026-01-30 | 100106 | Vibration | Misalignment corrected before seal and bearing damage | 18000 | 2500 | Engineering Manager
2026-02-25 | 100103 | Lubrication / oil | Contaminated oil changed; blower bearing saved | 65000 | 3000 | Engineering Manager
2026-04-10 | 100110 | Infrared | Overheating motor bearing replaced in planned window | 12000 | 1800 | Engineering Manager
2026-05-29 | 100302 | Infrared | Loose termination fixed before arc flash and MCC loss | 120000 | 800 | Engineering Manager
2026-06-02 | 100109 | Ultrasonics (airborne) | Under-lubrication corrected | 9000 | 300 | Engineering Manager
2026-06-20 | 100115 | Ultrasonics (airborne) | Compressed air leak repaired | 6000 | 400 | Engineering Manager
2026-08-28 | 100101 | Structural | Cracked structural support repaired | 40000 | 5000 | Engineering Manager
2026-09-14 | 100110 | Vibration | Worn coupling replaced before failure | 15000 | 1200 | Engineering Manager

## Programme_Cost
AHIM CM Programme Cost
Monthly cost of the condition monitoring and inspection programme (USD).
Month | Labour | Lab & consumables | Contractors | Equipment
2025-10-01 | 4200 | 1150 | 1500 | 300
2025-11-01 | 4200 | 1150 | 800 | 300
2025-12-01 | 4200 | 1150 | 0 | 300
2026-01-01 | 4200 | 1150 | 2400 | 300
2026-02-01 | 4200 | 1150 | 600 | 300
2026-03-01 | 4200 | 1150 | 1200 | 300
2026-04-01 | 4200 | 1150 | 0 | 300
2026-05-01 | 4200 | 1150 | 3000 | 300
2026-06-01 | 4200 | 1150 | 900 | 300
2026-07-01 | 4200 | 1150 | 1800 | 300
2026-08-01 | 4200 | 1150 | 500 | 300
2026-09-01 | 4200 | 1150 | 2100 | 300

## Decisions
AHIM Management Decisions
Decisions only management can make (stops, budget, statutory bookings). Status: Open, Approved, Rejected or Closed.
Date raised | Decision required | Reason | Owner | Status
2026-09-25 | Approve a 36-hour planned stop in October | Sulphur furnace refractory (340 °C hot spot) and acid line elbow E-07 (below minimum wall) cannot be repaired online. Both are P1. | Engineering and Production Managers | Open
2026-09-02 | Book the statutory inspector for the waste heat boiler | Certificate expires 22 Oct 2026. The boiler cannot legally operate after that date. | Engineering Manager | Open
2026-08-15 | Fund a fitness-for-service assessment on TK-01 | Product acid tank shell at 72% of nominal; recommendation open since April with no work order. | Engineering Manager | Open
2026-06-01 | Order a spare gearbox for cooling tower fan 1 | Gear damage confirmed by vibration and oil analysis; open since May. | Maintenance and Supply | Open
2026-05-02 | Approve ultrasound grease guns for lubrication route | Over- and under-greasing found on several bearings. | Engineering Manager | Approved

## Prestart
AHIM Prestart Compliance
Per month and vehicle/machine: shifts operated vs prestart checklists completed. Defects found go to Records.
Month | Pronto asset no. | Shifts operated | Prestarts completed
2025-10-01 | 100501 | 56 | 56
2025-10-01 | 100502 | 55 | 53
2025-10-01 | 100601 | 42 | 42
2025-10-01 | 100602 | 41 | 39
2025-10-01 | 100603 | 40 | 40
2025-11-01 | 100501 | 53 | 52
2025-11-01 | 100502 | 52 | 49
2025-11-01 | 100601 | 44 | 43
2025-11-01 | 100602 | 43 | 40
2025-11-01 | 100603 | 42 | 41
2025-12-01 | 100501 | 55 | 53
2025-12-01 | 100502 | 54 | 54
2025-12-01 | 100601 | 41 | 39
2025-12-01 | 100602 | 40 | 40
2025-12-01 | 100603 | 44 | 42
2026-01-01 | 100501 | 52 | 49
2026-01-01 | 100502 | 56 | 55
2026-01-01 | 100601 | 43 | 40
2026-01-01 | 100602 | 42 | 41
2026-01-01 | 100603 | 41 | 38
2026-02-01 | 100501 | 54 | 54
2026-02-01 | 100502 | 53 | 51
2026-02-01 | 100601 | 40 | 40
2026-02-01 | 100602 | 44 | 42
2026-02-01 | 100603 | 43 | 43
2026-03-01 | 100501 | 56 | 55
2026-03-01 | 100502 | 55 | 52
2026-03-01 | 100601 | 42 | 41
2026-03-01 | 100602 | 41 | 38
2026-03-01 | 100603 | 40 | 39
2026-04-01 | 100501 | 53 | 51
2026-04-01 | 100502 | 52 | 52
2026-04-01 | 100601 | 44 | 42
2026-04-01 | 100602 | 43 | 43
2026-04-01 | 100603 | 42 | 40
2026-05-01 | 100501 | 55 | 52
2026-05-01 | 100502 | 54 | 53
2026-05-01 | 100601 | 41 | 38
2026-05-01 | 100602 | 40 | 39
2026-05-01 | 100603 | 44 | 41
2026-06-01 | 100501 | 52 | 52
2026-06-01 | 100502 | 56 | 54
2026-06-01 | 100601 | 43 | 43
2026-06-01 | 100602 | 42 | 40
2026-06-01 | 100603 | 41 | 41
2026-07-01 | 100501 | 54 | 53
2026-07-01 | 100502 | 53 | 50
2026-07-01 | 100601 | 40 | 39
2026-07-01 | 100602 | 44 | 39
2026-07-01 | 100603 | 43 | 42
2026-08-01 | 100501 | 56 | 54
2026-08-01 | 100502 | 55 | 55
2026-08-01 | 100601 | 42 | 40
2026-08-01 | 100602 | 41 | 39
2026-08-01 | 100603 | 40 | 38
2026-09-01 | 100501 | 53 | 50
2026-09-01 | 100502 | 52 | 51
2026-09-01 | 100601 | 44 | 41
2026-09-01 | 100602 | 43 | 40
2026-09-01 | 100603 | 42 | 39

## Commentary
AHIM Monthly Analyst Commentary
One row per month: three short lines for management. Shown at the top of the Management page.
Month | What changed | Why | What we are doing | Author
2026-09-01 | AHI fell 6 points to 74. Four new Danger findings: drying tower pump bearing, MCC termination, acid line elbow below minimum wall, compactor brakes. | Late detection on two bad actors (P-101 repeat bearing failure; E-07 accelerated corrosion) and a backlog of 10 overdue recommendations. | 36-hour stop requested for October to repair furnace refractory and E-07. Weekly CM / planner review started to clear the backlog. | RCM Specialist

## Work_Orders
AHIM Work orders (from Pronto)
One row per work order. Filled automatically from the Pronto WO export in the CM workbook (WO Data) at each import; rows added here manually are kept. Source: Planner (Pronto saved report). Frequency: Weekly or monthly. Key: WO no..
WO no. | Pronto asset no. | Description | Work type | Priority | Status | Trade | Raised | Required by | Scheduled start | Actual finish | Planned hours | Actual hours | Downtime (h) | Failure code | Actual cost (USD) | Ready (Y/N) | Needs shutdown (Y/N) | AHIM finding ref
700001 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Open | Boilermaker | 2025-10-01 | 2025-10-28 | 2025-10-17 |  | 6 |  | 0 |  |  | Y | N
700002 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2025-10-01 | 2025-10-28 | 2025-10-17 | 2025-10-23 | 3 | 2.7 | 0 |  | 422 |  | N
700003 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-18 | 2025-10-19 | 2 | 2 | 0 |  | 90 |  | N
700004 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2025-10-01 | 2025-10-28 | 2025-10-05 | 2025-10-14 | 2 | 2.2 | 0 |  | 249 |  | N
700005 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-17 | 2025-10-23 | 3 | 3.3 | 0 |  | 448 |  | N
700006 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-05 | 2025-10-06 | 3 | 3.3 | 0 |  | 298 |  | N
700007 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-13 | 2025-10-14 | 8 | 7.3 | 0 |  | 408 |  | N
700008 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-18 | 2025-10-18 | 6 | 6.8 | 0 |  | 456 |  | N
700009 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Open | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-20 |  | 2 |  | 0 |  |  | Y | N
700010 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-11 | 2025-10-12 | 8 | 7.6 | 0 |  | 342 |  | N
700011 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-21 | 2025-10-24 | 2 | 2.4 | 0 |  | 258 |  | N
700012 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Open | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-05 |  | 2 |  | 0 |  |  | Y | N
700013 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2025-10-01 | 2025-10-28 | 2025-10-09 | 2025-10-09 | 6 | 5.9 | 0 |  | 416 |  | N
700014 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2025-10-01 | 2025-10-28 | 2025-10-16 | 2025-10-25 | 3 | 3.6 | 0 |  | 242 |  | N
700015 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2025-10-01 | 2025-10-28 | 2025-10-13 | 2025-10-15 | 2 | 2.6 | 0 |  | 117 |  | N
700016 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-07 | 2025-10-07 | 2 | 1.7 | 0 |  | 226 |  | N
700017 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2025-10-01 | 2025-10-28 | 2025-10-08 | 2025-10-09 | 6 | 6.3 | 0 |  | 284 |  | N
700018 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2025-10-01 | 2025-10-28 | 2025-10-16 | 2025-10-16 | 6 | 6.1 | 0 |  | 274 |  | N
700019 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-03 | 2025-10-09 | 4 | 5.2 | 0 |  | 234 |  | N
700020 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-09 | 2025-10-15 | 8 | 6.8 | 0 |  | 306 |  | N
700021 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-09 | 2025-10-09 | 8 | 7.7 | 0 |  | 426 |  | N
700022 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2025-10-01 | 2025-10-28 | 2025-10-15 | 2025-10-15 | 3 | 3.3 | 0 |  | 148 |  | N
700023 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2025-10-01 | 2025-10-28 | 2025-10-03 | 2025-10-05 | 8 | 8.2 | 0 |  | 669 |  | N
700024 | 100502 | Monthly PM LV-02 | Preventive | P3 | Open | Fleet | 2025-10-01 | 2025-10-28 | 2025-10-18 |  | 3 |  | 0 |  |  | Y | N
700025 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2025-10-01 | 2025-10-28 | 2025-10-15 | 2025-10-16 | 4 | 5 | 0 |  | 525 |  | N
700026 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2025-10-01 | 2025-10-28 | 2025-10-10 | 2025-10-11 | 8 | 7.2 | 0 |  | 474 |  | N
700027 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2025-10-01 | 2025-10-28 | 2025-10-18 | 2025-10-21 | 2 | 1.7 | 0 |  | 76 |  | N
700028 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Open | Boilermaker | 2025-11-01 | 2025-11-28 | 2025-11-19 |  | 3 |  | 0 |  |  | Y | N
700029 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2025-11-01 | 2025-11-28 | 2025-11-15 | 2025-11-21 | 6 | 5.7 | 0 |  | 256 |  | N
700030 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-05 | 2025-11-08 | 8 | 9 | 0 |  | 705 |  | N
700031 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2025-11-01 | 2025-11-28 | 2025-11-22 | 2025-11-23 | 3 | 3.5 | 0 |  | 158 |  | N
700032 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-11 | 2025-11-12 | 2 | 1.6 | 0 |  | 152 |  | N
700033 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-14 | 2025-11-15 | 2 | 2 | 0 |  | 240 |  | N
700034 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-13 | 2025-11-22 | 8 | 8.7 | 0 |  | 391 |  | N
700035 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-21 | 2025-11-21 | 6 | 7.5 | 0 |  | 418 |  | N
700036 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-04 | 2025-11-13 | 2 | 2.1 | 0 |  | 174 |  | N
700037 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-13 | 2025-11-13 | 2 | 2.1 | 0 |  | 174 |  | N
700038 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Open | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-04 |  | 3 |  | 0 |  |  | Y | N
700039 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-13 | 2025-11-22 | 6 | 7.5 | 0 |  | 488 |  | N
700040 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Open | Boilermaker | 2025-11-01 | 2025-11-28 | 2025-11-03 |  | 8 |  | 0 |  |  | Y | N
700041 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2025-11-01 | 2025-11-28 | 2025-11-03 | 2025-11-06 | 6 | 6.5 | 0 |  | 592 |  | N
700042 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2025-11-01 | 2025-11-28 | 2025-11-05 | 2025-11-14 | 2 | 2.6 | 0 |  | 267 |  | N
700043 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-13 | 2025-11-22 | 8 | 8.2 | 0 |  | 519 |  | N
700044 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2025-11-01 | 2025-11-28 | 2025-11-20 | 2025-11-26 | 2 | 1.9 | 0 |  | 86 |  | N
700045 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2025-11-01 | 2025-11-28 | 2025-11-18 | 2025-11-27 | 2 | 2.1 | 0 |  | 394 |  | N
700046 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Open | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-24 |  | 4 |  | 0 |  |  | Y | N
700047 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-03 | 2025-11-04 | 8 | 7.2 | 0 |  | 324 |  | N
700048 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-13 | 2025-11-16 | 6 | 7.5 | 0 |  | 418 |  | N
700049 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2025-11-01 | 2025-11-28 | 2025-11-15 | 2025-11-16 | 6 | 7.2 | 0 |  | 324 |  | N
700050 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2025-11-01 | 2025-11-28 | 2025-11-09 | 2025-11-15 | 4 | 3.6 | 0 |  | 162 |  | N
700051 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2025-11-01 | 2025-11-28 | 2025-11-18 | 2025-11-18 | 2 | 2.6 | 0 |  | 197 |  | N
700052 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2025-11-01 | 2025-11-28 | 2025-11-08 | 2025-11-11 | 4 | 5.1 | 0 |  | 380 |  | N
700053 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2025-11-01 | 2025-11-28 | 2025-11-15 | 2025-11-18 | 4 | 4.6 | 0 |  | 507 |  | N
700054 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2025-11-01 | 2025-11-28 | 2025-11-17 | 2025-11-17 | 4 | 4.9 | 0 |  | 221 |  | N
700055 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2025-12-01 | 2025-12-28 | 2025-12-24 | 2025-12-30 | 4 | 3.8 | 0 |  | 471 |  | N
700056 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2025-12-01 | 2025-12-28 | 2025-12-03 | 2025-12-06 | 6 | 5.4 | 0 |  | 323 |  | N
700057 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-10 | 2025-12-10 | 2 | 2 | 0 |  | 390 |  | N
700058 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2025-12-01 | 2025-12-28 | 2025-12-23 | 2025-12-25 | 2 | 2.3 | 0 |  | 103 |  | N
700059 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-18 | 2025-12-27 | 2 | 2.4 | 0 |  | 408 |  | N
700060 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-04 | 2025-12-06 | 4 | 4.3 | 0 |  | 494 |  | N
700061 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-19 | 2025-12-20 | 6 | 7.3 | 0 |  | 328 |  | N
700062 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-05 | 2025-12-14 | 6 | 5.2 | 0 |  | 384 |  | N
700063 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-09 | 2025-12-09 | 6 | 6.5 | 0 |  | 592 |  | N
700064 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-13 | 2025-12-22 | 3 | 2.5 | 0 |  | 112 |  | N
700065 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-09 | 2025-12-12 | 2 | 2.6 | 0 |  | 417 |  | N
700066 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-13 | 2025-12-22 | 2 | 1.9 | 0 |  | 86 |  | N
700067 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2025-12-01 | 2025-12-28 | 2025-12-04 | 2025-12-10 | 6 | 7.1 | 0 |  | 470 |  | N
700068 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2025-12-01 | 2025-12-28 | 2025-12-03 | 2025-12-03 | 6 | 7.2 | 0 |  | 324 |  | N
700069 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2025-12-01 | 2025-12-28 | 2025-12-20 | 2025-12-21 | 6 | 5.2 | 0 |  | 534 |  | N
700070 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Open | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-19 |  | 6 |  | 0 |  |  | Y | N
700071 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2025-12-01 | 2025-12-28 | 2025-12-18 | 2025-12-27 | 2 | 2.4 | 0 |  | 258 |  | N
700072 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2025-12-01 | 2025-12-28 | 2025-12-19 | 2025-12-28 | 8 | 9 | 0 |  | 705 |  | N
700073 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Open | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-19 |  | 8 |  | 0 |  |  | Y | N
700074 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-11 | 2025-12-14 | 8 | 7.2 | 0 |  | 324 |  | N
700075 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-20 | 2025-12-26 | 6 | 5.4 | 0 |  | 543 |  | N
700076 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2025-12-01 | 2025-12-28 | 2025-12-06 | 2025-12-12 | 6 | 4.9 | 0 |  | 221 |  | N
700077 | 100501 | Monthly PM LV-01 | Preventive | P3 | Open | Fleet | 2025-12-01 | 2025-12-28 | 2025-12-19 |  | 8 |  | 0 |  |  | Y | N
700078 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2025-12-01 | 2025-12-28 | 2025-12-21 | 2025-12-21 | 3 | 2.5 | 0 |  | 412 |  | N
700079 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2025-12-01 | 2025-12-28 | 2025-12-17 | 2025-12-20 | 4 | 3.7 | 0 |  | 316 |  | N
700080 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2025-12-01 | 2025-12-28 | 2025-12-07 | 2025-12-10 | 8 | 7.7 | 0 |  | 346 |  | N
700081 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2025-12-01 | 2025-12-28 | 2025-12-16 | 2025-12-18 | 3 | 3.5 | 0 |  | 158 |  | N
700082 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-01-01 | 2026-01-28 | 2026-01-04 | 2026-01-05 | 2 | 2.3 | 0 |  | 184 |  | N
700083 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-01-01 | 2026-01-28 | 2026-01-14 | 2026-01-17 | 2 | 2.1 | 0 |  | 394 |  | N
700084 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Open | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-06 |  | 8 |  | 0 |  |  | Y | N
700085 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-01-01 | 2026-01-28 | 2026-01-11 | 2026-01-20 | 8 | 9.9 | 0 |  | 446 |  | N
700086 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-15 | 2026-01-21 | 8 | 7 | 0 |  | 315 |  | N
700087 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-23 | 2026-01-24 | 8 | 7.3 | 0 |  | 628 |  | N
700088 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-22 | 2026-01-23 | 3 | 3.8 | 0 |  | 251 |  | N
700089 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-08 | 2026-01-10 | 3 | 2.7 | 0 |  | 122 |  | N
700090 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-06 | 2026-01-07 | 3 | 3.5 | 0 |  | 238 |  | N
700091 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-15 | 2026-01-18 | 8 | 9.6 | 0 |  | 432 |  | N
700092 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-09 | 2026-01-18 | 2 | 1.7 | 0 |  | 376 |  | N
700093 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-24 | 2026-01-26 | 2 | 2.3 | 0 |  | 184 |  | N
700094 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Open | Boilermaker | 2026-01-01 | 2026-01-28 | 2026-01-19 |  | 3 |  | 0 |  |  | Y | N
700095 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-01-01 | 2026-01-28 | 2026-01-05 | 2026-01-05 | 2 | 2.4 | 0 |  | 408 |  | N
700096 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Open | Boilermaker | 2026-01-01 | 2026-01-28 | 2026-01-19 |  | 6 |  | 0 |  |  | Y | N
700097 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-07 | 2026-01-07 | 3 | 2.7 | 0 |  | 122 |  | N
700098 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Open | Electrical | 2026-01-01 | 2026-01-28 | 2026-01-12 |  | 2 |  | 0 |  |  | Y | N
700099 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-01-01 | 2026-01-28 | 2026-01-21 | 2026-01-30 | 6 | 5 | 0 |  | 225 |  | N
700100 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-13 | 2026-01-16 | 8 | 7.8 | 0 |  | 351 |  | N
700101 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-22 | 2026-01-31 | 2 | 2.4 | 0 |  | 108 |  | N
700102 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-16 | 2026-01-25 | 4 | 4 | 0 |  | 180 |  | N
700103 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-01-01 | 2026-01-28 | 2026-01-22 | 2026-01-28 | 2 | 1.9 | 0 |  | 86 |  | N
700104 | 100501 | Monthly PM LV-01 | Preventive | P3 | Open | Fleet | 2026-01-01 | 2026-01-28 | 2026-01-23 |  | 8 |  | 0 |  |  | Y | N
700105 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-01-01 | 2026-01-28 | 2026-01-22 | 2026-01-28 | 4 | 4.8 | 0 |  | 296 |  | N
700106 | 100601 | Monthly PM HV-01 | Preventive | P3 | Open | Fleet | 2026-01-01 | 2026-01-28 | 2026-01-11 |  | 3 |  | 0 |  |  | Y | N
700107 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-01-01 | 2026-01-28 | 2026-01-15 | 2026-01-17 | 8 | 9.2 | 0 |  | 564 |  | N
700108 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-01-01 | 2026-01-28 | 2026-01-08 | 2026-01-17 | 3 | 2.5 | 0 |  | 192 |  | N
700109 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-02-01 | 2026-02-28 | 2026-02-12 | 2026-02-12 | 4 | 5.2 | 0 |  | 534 |  | N
700110 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-02-01 | 2026-02-28 | 2026-02-04 | 2026-02-13 | 4 | 3.9 | 0 |  | 326 |  | N
700111 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-21 | 2026-02-21 | 6 | 6.3 | 0 |  | 434 |  | N
700112 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-02-01 | 2026-02-28 | 2026-02-23 | 2026-02-23 | 6 | 7.7 | 0 |  | 346 |  | N
700113 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-06 | 2026-02-15 | 3 | 2.8 | 0 |  | 276 |  | N
700114 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-19 | 2026-02-20 | 6 | 4.8 | 0 |  | 296 |  | N
700115 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-11 | 2026-02-13 | 8 | 8.6 | 0 |  | 537 |  | N
700116 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-19 | 2026-02-19 | 6 | 7.2 | 0 |  | 324 |  | N
700117 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-20 | 2026-02-20 | 6 | 7.6 | 0 |  | 342 |  | N
700118 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-15 | 2026-02-16 | 6 | 6.4 | 0 |  | 588 |  | N
700119 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-04 | 2026-02-07 | 6 | 5.7 | 0 |  | 406 |  | N
700120 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-22 | 2026-02-28 | 4 | 4.2 | 0 |  | 269 |  | N
700121 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Open | Boilermaker | 2026-02-01 | 2026-02-28 | 2026-02-20 |  | 4 |  | 0 |  |  | Y | N
700122 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-02-01 | 2026-02-28 | 2026-02-03 | 2026-02-04 | 8 | 6.6 | 0 |  | 297 |  | N
700123 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-02-01 | 2026-02-28 | 2026-02-16 | 2026-02-19 | 2 | 2.5 | 0 |  | 262 |  | N
700124 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-04 | 2026-02-13 | 4 | 3.3 | 0 |  | 148 |  | N
700125 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2026-02-01 | 2026-02-28 | 2026-02-16 | 2026-02-18 | 3 | 2.5 | 0 |  | 112 |  | N
700126 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-02-01 | 2026-02-28 | 2026-02-17 | 2026-02-18 | 8 | 9.2 | 0 |  | 414 |  | N
700127 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-22 | 2026-02-22 | 3 | 3.7 | 0 |  | 246 |  | N
700128 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-19 | 2026-02-21 | 6 | 5.2 | 0 |  | 384 |  | N
700129 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-17 | 2026-02-26 | 8 | 9.1 | 0 |  | 490 |  | N
700130 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-02-01 | 2026-02-28 | 2026-02-19 | 2026-02-20 | 4 | 4.7 | 0 |  | 212 |  | N
700131 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2026-02-01 | 2026-02-28 | 2026-02-18 | 2026-02-20 | 8 | 8.9 | 0 |  | 480 |  | N
700132 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-02-01 | 2026-02-28 | 2026-02-11 | 2026-02-20 | 8 | 9.2 | 0 |  | 414 |  | N
700133 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-02-01 | 2026-02-28 | 2026-02-23 | 2026-02-24 | 3 | 3.8 | 0 |  | 471 |  | N
700134 | 100602 | Monthly PM HV-02 | Preventive | P3 | Open | Fleet | 2026-02-01 | 2026-02-28 | 2026-02-23 |  | 2 |  | 0 |  |  | Y | N
700135 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-02-01 | 2026-02-28 | 2026-02-23 | 2026-02-25 | 4 | 4.1 | 0 |  | 484 |  | N
700136 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-03-01 | 2026-03-28 | 2026-03-04 | 2026-03-10 | 4 | 3.3 | 0 |  | 148 |  | N
700137 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-03-01 | 2026-03-28 | 2026-03-24 | 2026-03-25 | 4 | 4.2 | 0 |  | 269 |  | N
700138 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-09 | 2026-03-12 | 3 | 3.7 | 0 |  | 166 |  | N
700139 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-03-01 | 2026-03-28 | 2026-03-06 | 2026-03-12 | 3 | 3.1 | 0 |  | 220 |  | N
700140 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-15 | 2026-03-17 | 3 | 3.4 | 0 |  | 453 |  | N
700141 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-13 | 2026-03-22 | 3 | 3 | 0 |  | 215 |  | N
700142 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-21 | 2026-03-23 | 2 | 2.1 | 0 |  | 244 |  | N
700143 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-21 | 2026-03-30 | 6 | 5.7 | 0 |  | 256 |  | N
700144 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-05 | 2026-03-14 | 8 | 6.7 | 0 |  | 382 |  | N
700145 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-18 | 2026-03-27 | 4 | 3.8 | 0 |  | 171 |  | N
700146 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-10 | 2026-03-19 | 4 | 3.9 | 0 |  | 176 |  | N
700147 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-13 | 2026-03-19 | 8 | 10.1 | 0 |  | 534 |  | N
700148 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2026-03-01 | 2026-03-28 | 2026-03-17 | 2026-03-19 | 6 | 5.8 | 0 |  | 411 |  | N
700149 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-03-01 | 2026-03-28 | 2026-03-19 | 2026-03-21 | 4 | 3.2 | 0 |  | 294 |  | N
700150 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-03-01 | 2026-03-28 | 2026-03-21 | 2026-03-22 | 8 | 7.9 | 0 |  | 506 |  | N
700151 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-20 | 2026-03-26 | 8 | 7.1 | 0 |  | 320 |  | N
700152 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Open | Electrical | 2026-03-01 | 2026-03-28 | 2026-03-17 |  | 4 |  | 0 |  |  | Y | N
700153 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-03-01 | 2026-03-28 | 2026-03-03 | 2026-03-03 | 8 | 7 | 0 |  | 395 |  | N
700154 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-03 | 2026-03-06 | 2 | 2.2 | 0 |  | 179 |  | N
700155 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-20 | 2026-03-20 | 4 | 4.7 | 0 |  | 292 |  | N
700156 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-05 | 2026-03-14 | 3 | 2.5 | 0 |  | 262 |  | N
700157 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-03-01 | 2026-03-28 | 2026-03-10 | 2026-03-13 | 8 | 7.8 | 0 |  | 501 |  | N
700158 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2026-03-01 | 2026-03-28 | 2026-03-15 | 2026-03-17 | 3 | 3.1 | 0 |  | 440 |  | N
700159 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-03-01 | 2026-03-28 | 2026-03-05 | 2026-03-05 | 6 | 7.1 | 0 |  | 400 |  | N
700160 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-03-01 | 2026-03-28 | 2026-03-03 | 2026-03-03 | 6 | 7.7 | 0 |  | 346 |  | N
700161 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-03-01 | 2026-03-28 | 2026-03-19 | 2026-03-19 | 2 | 2 | 0 |  | 240 |  | N
700162 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-03-01 | 2026-03-28 | 2026-03-07 | 2026-03-08 | 6 | 6.9 | 0 |  | 390 |  | N
700163 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-04-01 | 2026-04-28 | 2026-04-09 | 2026-04-15 | 4 | 3.7 | 0 |  | 166 |  | N
700164 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-04-01 | 2026-04-28 | 2026-04-18 | 2026-04-18 | 4 | 4.5 | 0 |  | 202 |  | N
700165 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-04 | 2026-04-04 | 8 | 8.3 | 0 |  | 374 |  | N
700166 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-04-01 | 2026-04-28 | 2026-04-13 | 2026-04-14 | 4 | 3.6 | 0 |  | 162 |  | N
700167 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-22 | 2026-04-28 | 8 | 7.3 | 0 |  | 328 |  | N
700168 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-11 | 2026-04-13 | 8 | 10.2 | 0 |  | 759 |  | N
700169 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-18 | 2026-04-21 | 6 | 7.5 | 0 |  | 418 |  | N
700170 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-24 | 2026-04-24 | 6 | 7.4 | 0 |  | 483 |  | N
700171 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-04 | 2026-04-05 | 6 | 7.7 | 0 |  | 646 |  | N
700172 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-11 | 2026-04-11 | 3 | 3.7 | 0 |  | 316 |  | N
700173 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-14 | 2026-04-15 | 6 | 6.6 | 0 |  | 297 |  | N
700174 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-16 | 2026-04-18 | 3 | 2.8 | 0 |  | 426 |  | N
700175 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2026-04-01 | 2026-04-28 | 2026-04-07 | 2026-04-13 | 4 | 4.2 | 0 |  | 189 |  | N
700176 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-04-01 | 2026-04-28 | 2026-04-07 | 2026-04-08 | 2 | 1.8 | 0 |  | 81 |  | N
700177 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-04-01 | 2026-04-28 | 2026-04-07 | 2026-04-09 | 8 | 9.3 | 0 |  | 419 |  | N
700178 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-18 | 2026-04-18 | 8 | 8.6 | 0 |  | 687 |  | N
700179 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2026-04-01 | 2026-04-28 | 2026-04-12 | 2026-04-13 | 6 | 5.4 | 0 |  | 243 |  | N
700180 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-04-01 | 2026-04-28 | 2026-04-17 | 2026-04-23 | 6 | 6.4 | 0 |  | 288 |  | N
700181 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-12 | 2026-04-15 | 2 | 2.2 | 0 |  | 249 |  | N
700182 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-24 | 2026-04-26 | 2 | 2.3 | 0 |  | 103 |  | N
700183 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-24 | 2026-04-27 | 2 | 2.3 | 0 |  | 103 |  | N
700184 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-04-01 | 2026-04-28 | 2026-04-15 | 2026-04-18 | 3 | 2.8 | 0 |  | 126 |  | N
700185 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2026-04-01 | 2026-04-28 | 2026-04-17 | 2026-04-26 | 3 | 3.8 | 0 |  | 171 |  | N
700186 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-04-01 | 2026-04-28 | 2026-04-12 | 2026-04-18 | 4 | 5.1 | 0 |  | 380 |  | N
700187 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-04-01 | 2026-04-28 | 2026-04-20 | 2026-04-22 | 3 | 2.7 | 0 |  | 122 |  | N
700188 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-04-01 | 2026-04-28 | 2026-04-13 | 2026-04-15 | 8 | 8.3 | 0 |  | 454 |  | N
700189 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-04-01 | 2026-04-28 | 2026-04-17 | 2026-04-17 | 2 | 1.7 | 0 |  | 76 |  | N
700190 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-05-01 | 2026-05-28 | 2026-05-07 | 2026-05-16 | 3 | 2.7 | 0 |  | 272 |  | N
700191 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-05-01 | 2026-05-28 | 2026-05-04 | 2026-05-10 | 2 | 1.7 | 0 |  | 76 |  | N
700192 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Open | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-08 |  | 6 |  | 0 |  |  | Y | N
700193 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-05-01 | 2026-05-28 | 2026-05-16 | 2026-05-18 | 6 | 7.6 | 0 |  | 342 |  | N
700194 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-23 | 2026-05-24 | 6 | 6.2 | 0 |  | 429 |  | N
700195 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-22 | 2026-05-25 | 8 | 9.2 | 0 |  | 414 |  | N
700196 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Open | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-24 |  | 8 |  | 0 |  |  | Y | N
700197 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-03 | 2026-05-04 | 4 | 3.8 | 0 |  | 321 |  | N
700198 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-06 | 2026-05-07 | 8 | 7.7 | 0 |  | 426 |  | N
700199 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-06 | 2026-05-07 | 4 | 4.7 | 0 |  | 292 |  | N
700200 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-20 | 2026-05-26 | 8 | 8.5 | 0 |  | 682 |  | N
700201 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Open | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-09 |  | 8 |  | 0 |  |  | Y | N
700202 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2026-05-01 | 2026-05-28 | 2026-05-09 | 2026-05-09 | 3 | 3.6 | 0 |  | 162 |  | N
700203 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-05-01 | 2026-05-28 | 2026-05-10 | 2026-05-13 | 4 | 3.9 | 0 |  | 256 |  | N
700204 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-05-01 | 2026-05-28 | 2026-05-11 | 2026-05-11 | 6 | 7.7 | 0 |  | 346 |  | N
700205 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Open | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-10 |  | 8 |  | 0 |  |  | Y | N
700206 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2026-05-01 | 2026-05-28 | 2026-05-20 | 2026-05-26 | 4 | 3.5 | 0 |  | 238 |  | N
700207 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-05-01 | 2026-05-28 | 2026-05-22 | 2026-05-22 | 4 | 4.6 | 0 |  | 287 |  | N
700208 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-10 | 2026-05-12 | 3 | 2.7 | 0 |  | 422 |  | N
700209 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-05 | 2026-05-08 | 3 | 3.6 | 0 |  | 162 |  | N
700210 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-12 | 2026-05-21 | 6 | 6.6 | 0 |  | 297 |  | N
700211 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-28 | 2026-05-08 | 2026-05-11 | 2 | 1.7 | 0 |  | 226 |  | N
700212 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2026-05-01 | 2026-05-28 | 2026-05-06 | 2026-05-07 | 4 | 4.2 | 0 |  | 269 |  | N
700213 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-05-01 | 2026-05-28 | 2026-05-10 | 2026-05-12 | 2 | 2.2 | 0 |  | 99 |  | N
700214 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-05-01 | 2026-05-28 | 2026-05-24 | 2026-05-27 | 6 | 6.6 | 0 |  | 447 |  | N
700215 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-05-01 | 2026-05-28 | 2026-05-14 | 2026-05-20 | 8 | 9.4 | 0 |  | 503 |  | N
700216 | 100603 | Monthly PM HV-03 | Preventive | P3 | Open | Fleet | 2026-05-01 | 2026-05-28 | 2026-05-18 |  | 6 |  | 0 |  |  | Y | N
700217 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-06-01 | 2026-06-28 | 2026-06-16 | 2026-06-16 | 8 | 6.9 | 0 |  | 610 |  | N
700218 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-06-01 | 2026-06-28 | 2026-06-13 | 2026-06-16 | 6 | 7.5 | 0 |  | 418 |  | N
700219 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-04 | 2026-06-10 | 6 | 7 | 0 |  | 615 |  | N
700220 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-06-01 | 2026-06-28 | 2026-06-13 | 2026-06-15 | 8 | 9.9 | 0 |  | 446 |  | N
700221 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-06 | 2026-06-07 | 8 | 9.9 | 0 |  | 446 |  | N
700222 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-18 | 2026-06-24 | 3 | 3.2 | 0 |  | 294 |  | N
700223 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-10 | 2026-06-19 | 4 | 4.9 | 0 |  | 370 |  | N
700224 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-21 | 2026-06-22 | 6 | 6.5 | 0 |  | 292 |  | N
700225 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-06 | 2026-06-07 | 2 | 2.5 | 0 |  | 412 |  | N
700226 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-17 | 2026-06-18 | 4 | 3.2 | 0 |  | 144 |  | N
700227 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-05 | 2026-06-08 | 8 | 8 | 0 |  | 440 |  | N
700228 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-21 | 2026-06-23 | 2 | 2.1 | 0 |  | 174 |  | N
700229 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2026-06-01 | 2026-06-28 | 2026-06-12 | 2026-06-13 | 6 | 7.4 | 0 |  | 333 |  | N
700230 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-06-01 | 2026-06-28 | 2026-06-12 | 2026-06-21 | 2 | 1.8 | 0 |  | 161 |  | N
700231 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-06-01 | 2026-06-28 | 2026-06-18 | 2026-06-27 | 8 | 7.2 | 0 |  | 324 |  | N
700232 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Open | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-09 |  | 2 |  | 0 |  |  | Y | N
700233 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2026-06-01 | 2026-06-28 | 2026-06-23 | 2026-07-02 | 4 | 5.1 | 0 |  | 310 |  | N
700234 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-06-01 | 2026-06-28 | 2026-06-16 | 2026-06-17 | 4 | 4.6 | 0 |  | 357 |  | N
700235 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-16 | 2026-06-17 | 4 | 3.4 | 0 |  | 153 |  | N
700236 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-11 | 2026-06-12 | 8 | 9.1 | 0 |  | 490 |  | N
700237 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-14 | 2026-06-20 | 2 | 2.2 | 0 |  | 99 |  | N
700238 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-06-01 | 2026-06-28 | 2026-06-12 | 2026-06-13 | 3 | 2.8 | 0 |  | 126 |  | N
700239 | 100501 | Monthly PM LV-01 | Preventive | P3 | Open | Fleet | 2026-06-01 | 2026-06-28 | 2026-06-17 |  | 6 |  | 0 |  |  | Y | N
700240 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-06-01 | 2026-06-28 | 2026-06-19 | 2026-06-19 | 2 | 2.2 | 0 |  | 179 |  | N
700241 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-06-01 | 2026-06-28 | 2026-06-20 | 2026-06-26 | 2 | 1.8 | 0 |  | 81 |  | N
700242 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-06-01 | 2026-06-28 | 2026-06-10 | 2026-06-19 | 8 | 6.5 | 0 |  | 292 |  | N
700243 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-06-01 | 2026-06-28 | 2026-06-04 | 2026-06-10 | 6 | 4.8 | 0 |  | 366 |  | N
700244 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-07-01 | 2026-07-28 | 2026-07-04 | 2026-07-10 | 4 | 3.8 | 0 |  | 321 |  | N
700245 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-07-01 | 2026-07-28 | 2026-07-04 | 2026-07-10 | 8 | 9.4 | 0 |  | 723 |  | N
700246 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-08 | 2026-07-09 | 2 | 2.2 | 0 |  | 99 |  | N
700247 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-07-01 | 2026-07-28 | 2026-07-24 | 2026-07-26 | 3 | 2.8 | 0 |  | 426 |  | N
700248 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-10 | 2026-07-16 | 6 | 5.6 | 0 |  | 252 |  | N
700249 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Open | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-22 |  | 2 |  | 0 |  |  | Y | N
700250 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-21 | 2026-07-22 | 4 | 3.5 | 0 |  | 158 |  | N
700251 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-22 | 2026-07-25 | 8 | 8.2 | 0 |  | 449 |  | N
700252 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-03 | 2026-07-04 | 8 | 9 | 0 |  | 705 |  | N
700253 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-10 | 2026-07-10 | 4 | 4.1 | 0 |  | 264 |  | N
700254 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-22 | 2026-07-24 | 8 | 8.4 | 0 |  | 678 |  | N
700255 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-08 | 2026-07-09 | 3 | 3.1 | 0 |  | 440 |  | N
700256 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2026-07-01 | 2026-07-28 | 2026-07-17 | 2026-07-20 | 6 | 5.9 | 0 |  | 266 |  | N
700257 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-07-01 | 2026-07-28 | 2026-07-04 | 2026-07-10 | 3 | 2.6 | 0 |  | 267 |  | N
700258 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-07-01 | 2026-07-28 | 2026-07-19 | 2026-07-19 | 2 | 1.8 | 0 |  | 381 |  | N
700259 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-07 | 2026-07-13 | 4 | 4.1 | 0 |  | 184 |  | N
700260 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2026-07-01 | 2026-07-28 | 2026-07-04 | 2026-07-13 | 8 | 7.3 | 0 |  | 408 |  | N
700261 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-07-01 | 2026-07-28 | 2026-07-06 | 2026-07-07 | 6 | 6.2 | 0 |  | 279 |  | N
700262 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-14 | 2026-07-20 | 3 | 2.5 | 0 |  | 262 |  | N
700263 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-21 | 2026-07-21 | 4 | 4.3 | 0 |  | 494 |  | N
700264 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-08 | 2026-07-11 | 3 | 3 | 0 |  | 135 |  | N
700265 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-28 | 2026-07-09 | 2026-07-10 | 3 | 3.6 | 0 |  | 162 |  | N
700266 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2026-07-01 | 2026-07-28 | 2026-07-18 | 2026-07-19 | 8 | 8.3 | 0 |  | 454 |  | N
700267 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-07-01 | 2026-07-28 | 2026-07-18 | 2026-07-27 | 3 | 3.7 | 0 |  | 166 |  | N
700268 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-07-01 | 2026-07-28 | 2026-07-20 | 2026-07-20 | 2 | 2.3 | 0 |  | 184 |  | N
700269 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-07-01 | 2026-07-28 | 2026-07-11 | 2026-07-17 | 3 | 3.5 | 0 |  | 458 |  | N
700270 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-07-01 | 2026-07-28 | 2026-07-15 | 2026-07-24 | 3 | 2.8 | 0 |  | 206 |  | N
700271 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-08-01 | 2026-08-28 | 2026-08-04 | 2026-08-06 | 3 | 3.5 | 0 |  | 158 |  | N
700272 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Open | Boilermaker | 2026-08-01 | 2026-08-28 | 2026-08-03 |  | 6 |  | 0 |  |  | Y | N
700273 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-17 | 2026-08-20 | 4 | 3.7 | 0 |  | 466 |  | N
700274 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-08-01 | 2026-08-28 | 2026-08-24 | 2026-08-27 | 8 | 7.4 | 0 |  | 333 |  | N
700275 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-09 | 2026-08-15 | 3 | 2.4 | 0 |  | 188 |  | N
700276 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-16 | 2026-08-22 | 3 | 3.2 | 0 |  | 444 |  | N
700277 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-11 | 2026-08-14 | 6 | 5.2 | 0 |  | 234 |  | N
700278 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-11 | 2026-08-14 | 6 | 5.2 | 0 |  | 534 |  | N
700279 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-14 | 2026-08-16 | 4 | 3.9 | 0 |  | 176 |  | N
700280 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-07 | 2026-08-07 | 6 | 6.5 | 0 |  | 372 |  | N
700281 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-24 | 2026-08-25 | 8 | 9.2 | 0 |  | 414 |  | N
700282 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-14 | 2026-08-23 | 4 | 3.4 | 0 |  | 303 |  | N
700283 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2026-08-01 | 2026-08-28 | 2026-08-06 | 2026-08-06 | 6 | 6 | 0 |  | 350 |  | N
700284 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-08-01 | 2026-08-28 | 2026-08-12 | 2026-08-14 | 3 | 2.6 | 0 |  | 267 |  | N
700285 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-08-01 | 2026-08-28 | 2026-08-09 | 2026-08-10 | 4 | 4.5 | 0 |  | 202 |  | N
700286 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-19 | 2026-08-21 | 6 | 7.2 | 0 |  | 474 |  | N
700287 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2026-08-01 | 2026-08-28 | 2026-08-21 | 2026-08-27 | 4 | 4.6 | 0 |  | 207 |  | N
700288 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Complete | Electrical | 2026-08-01 | 2026-08-28 | 2026-08-15 | 2026-08-15 | 6 | 5.6 | 0 |  | 402 |  | N
700289 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-18 | 2026-08-20 | 6 | 7 | 0 |  | 395 |  | N
700290 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-05 | 2026-08-07 | 4 | 5 | 0 |  | 525 |  | N
700291 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-12 | 2026-08-21 | 3 | 3.4 | 0 |  | 303 |  | N
700292 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-08-01 | 2026-08-28 | 2026-08-22 | 2026-08-24 | 2 | 2.2 | 0 |  | 99 |  | N
700293 | 100501 | Monthly PM LV-01 | Preventive | P3 | Complete | Fleet | 2026-08-01 | 2026-08-28 | 2026-08-05 | 2026-08-11 | 8 | 8 | 0 |  | 510 |  | N
700294 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-08-01 | 2026-08-28 | 2026-08-05 | 2026-08-08 | 6 | 5.9 | 0 |  | 416 |  | N
700295 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-08-01 | 2026-08-28 | 2026-08-04 | 2026-08-13 | 8 | 7.5 | 0 |  | 488 |  | N
700296 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-08-01 | 2026-08-28 | 2026-08-14 | 2026-08-14 | 3 | 3.3 | 0 |  | 228 |  | N
700297 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-08-01 | 2026-08-28 | 2026-08-10 | 2026-08-11 | 3 | 3.2 | 0 |  | 444 |  | N
700298 | 100101 | Monthly PM AP-SF-01 | Preventive | P3 | Complete | Boilermaker | 2026-09-01 | 2026-09-28 | 2026-09-15 | 2026-09-21 | 6 | 7.3 | 0 |  | 628 |  | N
700299 | 100102 | Monthly PM AP-WHB-01 | Preventive | P3 | Complete | Boilermaker | 2026-09-01 | 2026-09-28 | 2026-09-05 | 2026-09-11 | 4 | 3.7 | 0 |  | 166 |  | N
700300 | 100103 | Monthly PM AP-BL-01 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-03 | 2026-09-12 | 3 | 3.4 | 0 |  | 153 |  | N
700301 | 100104 | Monthly PM AP-CV-01 | Preventive | P3 | Complete | Boilermaker | 2026-09-01 | 2026-09-28 | 2026-09-09 | 2026-09-10 | 4 | 4.4 | 0 |  | 348 |  | N
700302 | 100105 | Monthly PM AP-P-101 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-21 | 2026-09-24 | 4 | 3.9 | 0 |  | 476 |  | N
700303 | 100106 | Monthly PM AP-P-102 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-18 | 2026-09-19 | 4 | 3.8 | 0 |  | 171 |  | N
700304 | 100107 | Monthly PM AP-P-103 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-19 | 2026-09-19 | 2 | 2.4 | 0 |  | 188 |  | N
700305 | 100108 | Monthly PM AP-P-201 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-06 | 2026-09-12 | 6 | 4.9 | 0 |  | 520 |  | N
700306 | 100109 | Monthly PM AP-P-202 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-16 | 2026-09-16 | 4 | 3.7 | 0 |  | 466 |  | N
700307 | 100110 | Monthly PM AP-P-301 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-15 | 2026-09-24 | 4 | 3.9 | 0 |  | 256 |  | N
700308 | 100111 | Monthly PM AP-AG-01 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-08 | 2026-09-09 | 8 | 9.7 | 0 |  | 736 |  | N
700309 | 100112 | Monthly PM AP-CT-01 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-16 | 2026-09-17 | 8 | 9.4 | 0 |  | 503 |  | N
700310 | 100113 | Monthly PM AP-TK-01 | Preventive | P3 | Complete | Boilermaker | 2026-09-01 | 2026-09-28 | 2026-09-08 | 2026-09-11 | 8 | 9.1 | 0 |  | 410 |  | N
700311 | 100114 | Monthly PM AP-PL-01 | Preventive | P3 | Complete | Boilermaker | 2026-09-01 | 2026-09-28 | 2026-09-23 | 2026-09-23 | 6 | 6.6 | 0 |  | 297 |  | N
700312 | 100115 | Monthly PM AP-AR-01 | Preventive | P3 | Complete | Boilermaker | 2026-09-01 | 2026-09-28 | 2026-09-11 | 2026-09-14 | 4 | 4.5 | 0 |  | 352 |  | N
700313 | 100201 | Monthly PM CK-1080 | Preventive | P3 | Scheduled | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-15 |  | 3 |  | 0 |  |  | Y | N
700314 | 100301 | Monthly PM SS-TX-01 | Preventive | P3 | Complete | Electrical | 2026-09-01 | 2026-09-28 | 2026-09-04 | 2026-09-04 | 2 | 1.8 | 0 |  | 161 |  | N
700315 | 100302 | Monthly PM SS-MCC-01 | Preventive | P3 | Scheduled | Electrical | 2026-09-01 | 2026-09-28 | 2026-09-20 |  | 2 |  | 0 |  |  | Y | N
700316 | 100401 | Monthly PM PP-GEN-01 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-15 | 2026-09-15 | 8 | 9.8 | 0 |  | 441 |  | N
700317 | 100402 | Monthly PM PP-GEN-02 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-14 | 2026-09-17 | 4 | 3.6 | 0 |  | 462 |  | N
700318 | 100403 | Monthly PM PP-GEN-03 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-16 | 2026-09-22 | 6 | 6.8 | 0 |  | 306 |  | N
700319 | 100404 | Monthly PM PP-GEN-04 | Preventive | P3 | Complete | Mechanical | 2026-09-01 | 2026-09-28 | 2026-09-20 | 2026-09-21 | 6 | 5.3 | 0 |  | 238 |  | N
700320 | 100501 | Monthly PM LV-01 | Preventive | P3 | Scheduled | Fleet | 2026-09-01 | 2026-09-28 | 2026-09-20 |  | 4 |  | 0 |  |  | Y | N
700321 | 100502 | Monthly PM LV-02 | Preventive | P3 | Complete | Fleet | 2026-09-01 | 2026-09-28 | 2026-09-18 | 2026-09-19 | 4 | 5 | 0 |  | 305 |  | N
700322 | 100601 | Monthly PM HV-01 | Preventive | P3 | Complete | Fleet | 2026-09-01 | 2026-09-28 | 2026-09-21 | 2026-09-23 | 6 | 5.6 | 0 |  | 252 |  | N
700323 | 100602 | Monthly PM HV-02 | Preventive | P3 | Complete | Fleet | 2026-09-01 | 2026-09-28 | 2026-09-05 | 2026-09-07 | 8 | 7.4 | 0 |  | 333 |  | N
700324 | 100603 | Monthly PM HV-03 | Preventive | P3 | Complete | Fleet | 2026-09-01 | 2026-09-28 | 2026-09-07 | 2026-09-09 | 2 | 1.6 | 0 |  | 152 |  | N
242210 | 100106 | Laser align pump and motor | Condition-based | P2 | Complete | Mechanical | 2026-01-14 | 2026-02-13 | 2026-01-20 | 2026-01-30 | 6 | 8.4 | 0 |  | 2203 |  | N | Alignment condition
242530 | 100103 | Change oil and filters | Condition-based | P2 | Complete | Mechanical | 2026-02-07 | 2026-03-09 | 2026-02-18 | 2026-02-25 | 8 | 8.8 | 0 |  | 876 |  | Y | Oil contamination
243120 | 100301 | Clean and retorque connection | Condition-based | P2 | Complete | Electrical | 2026-03-01 | 2026-03-31 | 2026-03-08 | 2026-04-15 | 16 | 16.6 | 0 |  | 2271 |  | N | LV bushing connectio
242980 | 100110 | Replace motor bearing in planned window | Condition-based | P2 | Complete | Mechanical | 2026-03-24 | 2026-04-23 | 2026-04-07 | 2026-04-10 | 16 | 14.8 | 0 |  | 1189 |  | N | Motor DE bearing tem
243305 | 100201 | Clean gear and reapply lubricant | Condition-based | P2 | Complete | Mechanical | 2026-04-10 | 2026-05-10 | 2026-04-23 | 2026-05-20 | 4 | 3.7 | 0 |  | 1890 |  | Y | Girth gear lubricant
243766 | 100112 | Borescope gearbox; plan overhaul and order spare | Condition-based | P2 | Scheduled | Mechanical | 2026-05-15 | 2026-06-14 | 2026-05-19 |  | 8 |  | 0 |  |  | Y | N | Gearbox overall velo
243767 | 100112 | Oil change; trend wear metals monthly | Condition-based | P2 | Scheduled | Mechanical | 2026-05-11 | 2026-06-10 | 2026-05-15 |  | 6 |  | 0 |  |  | Y | N | Copper (Cu) in gearb
243620 | 100109 | Regrease by ultrasound | Condition-based | P2 | Complete | Mechanical | 2026-05-13 | 2026-06-12 | 2026-05-20 | 2026-06-02 | 16 | 20.9 | 0 |  | 3107 |  | N | NDE bearing lubricat
243910 | 100302 | Re-terminate lug | Condition-based | P2 | Complete | Electrical | 2026-05-29 | 2026-06-28 | 2026-06-08 | 2026-05-29 | 4 | 4.4 | 0 |  | 2093 |  | Y | Hottest termination
243955 | 100115 | Replace drain valve | Condition-based | P2 | Complete | Boilermaker | 2026-06-06 | 2026-07-06 | 2026-06-09 | 2026-06-20 | 4 | 4.8 | 0 |  | 1350 |  | N | Leak survey level
244402 | 100108 | Retorque base bolts | Condition-based | P2 | Complete | Mechanical | 2026-07-08 | 2026-08-07 | 2026-07-19 | 2026-08-12 | 8 | 9.8 | 0 |  | 2133 |  | N | Overall velocity (ma
244150 | 100111 | Flush oil and replace breather | Condition-based | P2 | Complete | Mechanical | 2026-07-19 | 2026-08-18 | 2026-07-26 | 2026-08-30 | 8 | 8.3 | 0 |  | 3316 |  | N | Particle count
244512 | 100104 | Hot-retorque flange bolts; check gasket | Condition-based | P2 | Scheduled | Boilermaker | 2026-07-21 | 2026-08-20 | 2026-07-29 |  | 8 |  | 0 |  |  | Y | Y | Bed 3 outlet flange
244380 | 100101 | Repair weld; MPI after repair | Condition-based | P2 | Complete | Boilermaker | 2026-08-05 | 2026-09-04 | 2026-08-08 | 2026-08-28 | 6 | 7.6 | 0 |  | 2767 |  | N | Burner platform supp
244620 | 100502 | Replace seatbelt buckle | Condition-based | P2 | Complete | Fleet | 2026-08-13 | 2026-09-12 | 2026-08-21 | 2026-08-12 | 6 | 5.7 | 0 |  | 1115 |  | N | Seatbelt
244690 | 100106 | Change oil | Condition-based | P2 | Complete | Mechanical | 2026-08-20 | 2026-09-19 | 2026-08-23 | 2026-09-10 | 12 | 10.9 | 0 |  | 2918 |  | Y | Oil oxidation
244720 | 100104 | Replace gasket at opportunity | Condition-based | P2 | Complete | Boilermaker | 2026-08-21 | 2026-09-20 | 2026-09-01 | 2026-09-25 | 8 | 10.6 | 0 |  | 1478 |  | Y | Manway gasket
244871 | 100301 | Clean and retorque at next outage | Condition-based | P2 | Ready | Electrical | 2026-08-26 | 2026-09-25 | 2026-08-30 |  | 8 |  | 0 |  |  | Y | N | LV bushing connectio
244930 | 100102 | Book statutory inspector; prepare hydro test | Condition-based | P2 | Scheduled | Boilermaker | 2026-09-02 | 2026-10-02 | 2026-09-10 |  | 16 |  | 0 |  |  | Y | N | Pressure vessel cert
244950 | 100110 | Replace coupling element | Condition-based | P2 | Complete | Mechanical | 2026-09-03 | 2026-10-03 | 2026-09-12 | 2026-09-14 | 12 | 15.5 | 0 |  | 1588 |  | N | Coupling condition
245044 | 100108 | Change oil; fit desiccant breather; check seal | Condition-based | P2 | Ready | Mechanical | 2026-09-06 | 2026-10-06 | 2026-09-14 |  | 12 |  | 0 |  |  | Y | N | Water in bearing oil
245011 | 100101 | Refractory inspection at next stop; daily IR until then | Condition-based | P2 | Scheduled | Boilermaker | 2026-09-11 | 2026-10-11 | 2026-09-14 |  | 16 |  | 0 |  |  | Y | Y | Burner-end shell tem
245102 | 100103 | Clean impeller; trim balance at next stop | Condition-based | P2 | Ready | Mechanical | 2026-09-18 | 2026-10-18 | 2026-10-01 |  | 12 |  | 0 |  |  | Y | Y | Overall velocity (ma
245207 | 100114 | Replace elbow spool; extend UT grid +/-1 m | Condition-based | P2 | Scheduled | Boilermaker | 2026-09-23 | 2026-10-23 | 2026-10-01 |  | 16 |  | 0 |  |  | Y | N | Elbow E-07 wall
245289 | 100105 | Replace DE bearing; check alignment and soft foot | Condition-based | P2 | Ready | Mechanical | 2026-09-28 | 2026-10-28 | 2026-10-09 |  | 12 |  | 0 |  |  | Y | N | Overall velocity (ma
245290 | 100105 | Oil change and filter; resample in 2 weeks | Condition-based | P2 | Complete | Mechanical | 2026-09-23 | 2026-10-23 | 2026-10-07 | 2026-09-28 | 4 | 5 | 0 |  | 2276 |  | N | Iron (Fe)
245318 | 100302 | Isolate, re-terminate and torque lugs; re-scan | Condition-based | P2 | Ready | Electrical | 2026-09-28 | 2026-10-28 | 2026-10-07 |  | 12 |  | 0 |  |  | Y | N | Hottest termination
245402 | 100602 | Repair brakes before operation; verify by mechanic | Condition-based | P2 | Ready | Fleet | 2026-10-03 | 2026-11-02 | 2026-10-14 |  | 16 |  | 0 |  |  | Y | N | Service brake
241210 | 100110 | Steam jacket leak, pump stopped | Breakdown | P1 | Complete | Mechanical | 2025-11-30 | 2025-11-30 | 2025-11-30 | 2025-11-30 05:00 | 5 | 8 | 5 | BRD | 11454 |  | N
241260 | 100404 | Fuel injector failure, unit offline | Breakdown | P1 | Complete | Mechanical | 2025-12-05 | 2025-12-05 | 2025-12-05 | 2025-12-05 10:00 | 10 | 16 | 10 | VIB | 10920 |  | N
241300 | 100105 | Mechanical seal leak | Breakdown | P1 | Complete | Mechanical | 2025-12-10 | 2025-12-10 | 2025-12-10 | 2025-12-10 08:00 | 8 | 12.8 | 8 | OHE | 13001 |  | N
241350 | 100201 | Girth gear lubrication spray failure | Breakdown | P1 | Complete | Mechanical | 2025-12-15 | 2025-12-15 | 2025-12-15 | 2025-12-15 18:00 | 18 | 28.8 | 18 | BRD | 14621 |  | N
242100 | 100112 | Fan blade pitch slipped, high vibration trip | Breakdown | P1 | Complete | Mechanical | 2026-01-08 | 2026-01-08 | 2026-01-08 | 2026-01-08 04:00 | 4 | 6.4 | 4 | BRD | 7960 |  | N
242150 | 100107 | Impeller wear, low discharge pressure | Breakdown | P1 | Complete | Mechanical | 2026-01-12 | 2026-01-12 | 2026-01-12 | 2026-01-12 10:00 | 10 | 16 | 10 | ELP | 12397 |  | N
242300 | 100103 | Inlet guide vane actuator seized, blower tripped | Breakdown | P1 | Complete | Mechanical | 2026-01-20 | 2026-01-20 | 2026-01-20 | 2026-01-20 06:00 | 6 | 9.6 | 6 | VIB | 8336 |  | N
242400 | 100601 | Hydraulic hose burst | Breakdown | P1 | Complete | Fleet | 2026-02-10 | 2026-02-10 | 2026-02-10 | 2026-02-10 06:00 | 6 | 9.6 | 6 | OHE | 15051 |  | N
242450 | 100102 | Economiser tube leak, plant stopped | Breakdown | P1 | Complete | Boilermaker | 2026-02-14 | 2026-02-14 | 2026-02-14 | 2026-02-15 12:00 | 36 | 57.6 | 36 | OHE | 10845 |  | N
242600 | 100302 | Feeder F-07 contactor burned, trip | Breakdown | P1 | Complete | Electrical | 2026-02-20 | 2026-02-20 | 2026-02-20 | 2026-02-20 03:00 | 4 | 6.4 | 3 | VIB | 11678 |  | N
242800 | 100401 | Turbocharger oil feed line leak, unit stopped | Breakdown | P1 | Complete | Mechanical | 2026-03-11 | 2026-03-11 | 2026-03-11 | 2026-03-11 20:00 | 20 | 32 | 20 | VIB | 6059 |  | N
243250 | 100105 | DE bearing failure | Breakdown | P1 | Complete | Mechanical | 2026-04-22 | 2026-04-22 | 2026-04-22 | 2026-04-22 14:00 | 14 | 22.4 | 14 | ELP | 16574 |  | N
243900 | 100404 | Coolant hose burst, high temperature trip | Breakdown | P1 | Complete | Mechanical | 2026-06-18 | 2026-06-18 | 2026-06-18 | 2026-06-18 08:00 | 8 | 12.8 | 8 | VIB | 5099 |  | N
244200 | 100114 | Pinhole leak at elbow E-04, line isolated | Breakdown | P1 | Complete | Boilermaker | 2026-07-05 | 2026-07-05 | 2026-07-05 | 2026-07-05 12:00 | 12 | 19.2 | 12 | ELP | 6982 |  | N
244300 | 100602 | Alternator failure | Breakdown | P1 | Complete | Fleet | 2026-07-22 | 2026-07-22 | 2026-07-22 | 2026-07-22 05:00 | 5 | 8 | 5 | ELP | 4676 |  | N
700325 | 100104 | Corrective work on AP-CV-01 | Corrective | P2 | Complete | Boilermaker | 2025-10-17 | 2025-11-16 | 2025-10-29 | 2025-10-23 | 40 | 41.6 | 0 |  | 6340 |  | N
700326 | 100602 | Corrective work on HV-02 | Corrective | P3 | Complete | Fleet | 2025-10-12 | 2025-11-11 | 2025-10-17 | 2025-10-26 | 8 | 11.8 | 0 |  | 2454 |  | N
700327 | 100103 | Corrective work on AP-BL-01 | Corrective | P2 | Open | Mechanical | 2025-10-04 | 2025-11-03 | 2025-10-17 |  | 16 |  | 0 |  |  |  | N
700328 | 100201 | Emergency work on CK-1080 | Emergency | P1 | Complete | Mechanical | 2025-10-02 | 2025-10-09 | 2025-10-05 | 2025-10-05 | 40 | 54.7 | 0 |  | 2921 |  | N
700329 | 100111 | Improvement work on AP-AG-01 | Improvement | P2 | Ready | Mechanical | 2025-10-02 | 2025-11-01 | 2025-10-09 |  | 8 |  | 0 |  |  | Y | N
700330 | 100106 | Corrective work on AP-P-102 | Corrective | P3 | Scheduled | Mechanical | 2025-10-20 | 2025-11-19 | 2025-10-22 |  | 24 |  | 0 |  |  | Y | N
700331 | 100103 | Corrective work on AP-BL-01 | Corrective | P3 | Complete | Mechanical | 2025-10-21 | 2025-11-20 | 2025-10-28 | 2025-11-14 | 8 | 6.5 | 0 |  | 3281 |  | N
700332 | 100501 | Emergency work on LV-01 | Emergency | P1 | Open | Fleet | 2025-10-11 | 2025-10-18 | 2025-10-23 |  | 32 |  | 0 |  |  |  | N
700333 | 100106 | Corrective work on AP-P-102 | Corrective | P2 | Open | Mechanical | 2025-10-25 | 2025-11-24 | 2025-10-30 |  | 16 |  | 0 |  |  |  | N
700334 | 100104 | Improvement work on AP-CV-01 | Improvement | P2 | Complete | Boilermaker | 2025-10-09 | 2025-11-08 | 2025-10-10 | 2025-10-21 | 12 | 18 | 0 |  | 6366 |  | N
700335 | 100107 | Emergency work on AP-P-103 | Emergency | P1 | Scheduled | Mechanical | 2025-10-24 | 2025-10-31 | 2025-10-28 |  | 40 |  | 0 |  |  | Y | N
700336 | 100103 | Corrective work on AP-BL-01 | Corrective | P3 | Complete | Mechanical | 2025-10-21 | 2025-11-20 | 2025-10-29 | 2025-11-10 | 16 | 14.3 | 0 |  | 1912 |  | N
700337 | 100104 | Corrective work on AP-CV-01 | Corrective | P2 | Complete | Boilermaker | 2025-10-12 | 2025-11-11 | 2025-10-17 | 2025-10-28 | 24 | 21.3 | 0 |  | 3646 |  | N
700338 | 100103 | Corrective work on AP-BL-01 | Corrective | P2 | Complete | Mechanical | 2025-10-22 | 2025-11-21 | 2025-11-03 | 2025-11-07 | 16 | 17.4 | 0 |  | 2705 |  | N
700339 | 100115 | Corrective work on AP-AR-01 | Corrective | P3 | Complete | Boilermaker | 2025-10-21 | 2025-11-20 | 2025-11-01 | 2025-10-31 | 24 | 35.2 | 0 |  | 3699 |  | N
700340 | 100404 | Corrective work on PP-GEN-04 | Corrective | P3 | Complete | Mechanical | 2025-10-23 | 2025-11-22 | 2025-10-26 | 2025-10-24 | 16 | 19.4 | 0 |  | 2961 |  | N
700341 | 100113 | Corrective work on AP-TK-01 | Corrective | P2 | Complete | Boilermaker | 2025-10-14 | 2025-11-13 | 2025-10-23 | 2025-11-08 | 24 | 30.2 | 0 |  | 5012 |  | N
700342 | 100107 | Emergency work on AP-P-103 | Emergency | P1 | Complete | Mechanical | 2025-10-03 | 2025-10-10 | 2025-10-13 | 2025-10-04 | 32 | 40.6 | 0 |  | 1890 |  | N
700343 | 100404 | Corrective work on PP-GEN-04 | Corrective | P3 | Complete | Mechanical | 2025-10-21 | 2025-11-20 | 2025-10-29 | 2025-10-27 | 16 | 20.3 | 0 |  | 5860 |  | N
700344 | 100102 | Improvement work on AP-WHB-01 | Improvement | P2 | Scheduled | Boilermaker | 2025-10-08 | 2025-11-07 | 2025-10-19 |  | 16 |  | 0 |  |  | Y | N
700345 | 100302 | Corrective work on SS-MCC-01 | Corrective | P3 | Complete | Electrical | 2025-10-23 | 2025-11-22 | 2025-11-05 | 2025-11-07 | 32 | 40.3 | 0 |  | 3486 |  | N
700346 | 100401 | Corrective work on PP-GEN-01 | Corrective | P2 | Scheduled | Mechanical | 2025-11-07 | 2025-12-07 | 2025-11-19 |  | 24 |  | 0 |  |  | Y | N
700347 | 100602 | Corrective work on HV-02 | Corrective | P3 | Ready | Fleet | 2025-11-03 | 2025-12-03 | 2025-11-16 |  | 32 |  | 0 |  |  | Y | N
700348 | 100104 | Corrective work on AP-CV-01 | Corrective | P2 | Complete | Boilermaker | 2025-11-14 | 2025-12-14 | 2025-11-16 | 2025-11-26 | 40 | 41.8 | 0 |  | 6489 |  | N
700349 | 100302 | Improvement work on SS-MCC-01 | Improvement | P2 | Ready | Electrical | 2025-11-18 | 2025-12-18 | 2025-11-20 |  | 4 |  | 0 |  |  | Y | N
700350 | 100401 | Corrective work on PP-GEN-01 | Corrective | P3 | Complete | Mechanical | 2025-11-08 | 2025-12-08 | 2025-11-14 | 2025-11-25 | 12 | 16.1 | 0 |  | 2721 |  | N
700351 | 100401 | Corrective work on PP-GEN-01 | Corrective | P2 | Scheduled | Mechanical | 2025-11-14 | 2025-12-14 | 2025-11-23 |  | 24 |  | 0 |  |  | Y | N
700352 | 100104 | Corrective work on AP-CV-01 | Corrective | P2 | Open | Boilermaker | 2025-11-15 | 2025-12-15 | 2025-11-25 |  | 40 |  | 0 |  |  |  | N
700353 | 100301 | Corrective work on SS-TX-01 | Corrective | P3 | Complete | Electrical | 2025-11-06 | 2025-12-06 | 2025-11-20 | 2025-11-29 | 4 | 3.2 | 0 |  | 1559 |  | N
700354 | 100602 | Emergency work on HV-02 | Emergency | P1 | Ready | Fleet | 2025-11-04 | 2025-11-11 | 2025-11-13 |  | 8 |  | 4 |  |  | Y | N
700355 | 100101 | Corrective work on AP-SF-01 | Corrective | P2 | Complete | Boilermaker | 2025-11-13 | 2025-12-13 | 2025-11-20 | 2025-12-01 | 32 | 34.9 | 0 |  | 2341 |  | N
700356 | 100107 | Corrective work on AP-P-103 | Corrective | P3 | Complete | Mechanical | 2025-11-09 | 2025-12-09 | 2025-11-13 | 2025-11-23 | 12 | 15.1 | 0 |  | 5288 |  | N
700357 | 100105 | Improvement work on AP-P-101 | Improvement | P3 | Scheduled | Mechanical | 2025-11-19 | 2025-12-19 | 2025-11-24 |  | 4 |  | 0 |  |  | Y | N
700358 | 100502 | Corrective work on LV-02 | Corrective | P3 | Complete | Fleet | 2025-11-20 | 2025-12-20 | 2025-11-27 | 2025-12-04 | 40 | 42 | 0 |  | 5626 |  | N
700359 | 100111 | Corrective work on AP-AG-01 | Corrective | P2 | Complete | Mechanical | 2025-11-15 | 2025-12-15 | 2025-11-24 | 2025-12-02 | 4 | 4.3 | 0 |  | 2943 |  | N
700360 | 100113 | Emergency work on AP-TK-01 | Emergency | P1 | Ready | Boilermaker | 2025-11-08 | 2025-11-15 | 2025-11-14 |  | 4 |  | 2 |  |  | Y | N
700361 | 100108 | Emergency work on AP-P-201 | Emergency | P1 | Complete | Mechanical | 2025-11-17 | 2025-11-24 | 2025-11-24 | 2025-11-18 | 12 | 14.6 | 0 |  | 757 |  | N
700362 | 100501 | Corrective work on LV-01 | Corrective | P3 | Complete | Fleet | 2025-11-19 | 2025-12-19 | 2025-12-03 | 2025-12-09 | 32 | 32.3 | 0 |  | 6690 |  | N
700363 | 100601 | Corrective work on HV-01 | Corrective | P3 | Complete | Fleet | 2025-11-19 | 2025-12-19 | 2025-11-20 | 2025-11-23 | 24 | 33.6 | 0 |  | 3047 |  | N
700364 | 100109 | Corrective work on AP-P-202 | Corrective | P3 | Ready | Mechanical | 2025-11-19 | 2025-12-19 | 2025-11-21 |  | 16 |  | 0 |  |  | Y | N
700365 | 100401 | Corrective work on PP-GEN-01 | Corrective | P3 | Complete | Mechanical | 2025-12-22 | 2026-01-21 | 2025-12-28 | 2025-12-30 | 40 | 32.9 | 0 |  | 3323 |  | N
700366 | 100603 | Emergency work on HV-03 | Emergency | P1 | Complete | Fleet | 2025-12-05 | 2025-12-12 | 2025-12-13 | 2025-12-07 | 40 | 33.3 | 4 |  | 2786 |  | N
700367 | 100302 | Improvement work on SS-MCC-01 | Improvement | P2 | Complete | Electrical | 2025-12-05 | 2026-01-04 | 2025-12-15 | 2025-12-06 | 24 | 28.4 | 0 |  | 5225 |  | N
700368 | 100114 | Emergency work on AP-PL-01 | Emergency | P1 | Open | Boilermaker | 2025-12-11 | 2025-12-18 | 2025-12-14 |  | 40 |  | 0 |  |  |  | N
700369 | 100115 | Emergency work on AP-AR-01 | Emergency | P1 | Complete | Boilermaker | 2025-12-22 | 2025-12-29 | 2025-12-29 | 2026-01-06 | 32 | 43.5 | 2 |  | 4320 |  | N
700370 | 100502 | Corrective work on LV-02 | Corrective | P2 | Complete | Fleet | 2025-12-24 | 2026-01-23 | 2026-01-05 | 2026-01-05 | 32 | 28.3 | 0 |  | 4239 |  | N
700371 | 100501 | Corrective work on LV-01 | Corrective | P3 | Open | Fleet | 2025-12-21 | 2026-01-20 | 2025-12-27 |  | 8 |  | 0 |  |  |  | N
700372 | 100302 | Emergency work on SS-MCC-01 | Emergency | P1 | Complete | Electrical | 2025-12-05 | 2025-12-12 | 2025-12-12 | 2025-12-14 | 16 | 13.2 | 2 |  | 3992 |  | N
700373 | 100107 | Emergency work on AP-P-103 | Emergency | P1 | Complete | Mechanical | 2025-12-22 | 2025-12-29 | 2026-01-04 | 2026-01-05 | 32 | 34.3 | 2 |  | 2562 |  | N
700374 | 100302 | Emergency work on SS-MCC-01 | Emergency | P1 | Open | Electrical | 2025-12-24 | 2025-12-31 | 2025-12-25 |  | 12 |  | 0 |  |  |  | N
700375 | 100603 | Corrective work on HV-03 | Corrective | P3 | Complete | Fleet | 2025-12-06 | 2026-01-05 | 2025-12-14 | 2025-12-23 | 32 | 38.5 | 0 |  | 5486 |  | N
700376 | 100112 | Corrective work on AP-CT-01 | Corrective | P2 | Complete | Mechanical | 2025-12-25 | 2026-01-24 | 2026-01-06 | 2026-01-07 | 12 | 13.7 | 0 |  | 5880 |  | N
700377 | 100109 | Emergency work on AP-P-202 | Emergency | P1 | Complete | Mechanical | 2025-12-12 | 2025-12-19 | 2025-12-25 | 2025-12-21 | 4 | 5.5 | 2 |  | 2292 |  | N
700378 | 100501 | Corrective work on LV-01 | Corrective | P3 | Complete | Fleet | 2025-12-07 | 2026-01-06 | 2025-12-16 | 2025-12-25 | 8 | 9 | 0 |  | 4487 |  | N
700379 | 100104 | Corrective work on AP-CV-01 | Corrective | P2 | Complete | Boilermaker | 2025-12-08 | 2026-01-07 | 2025-12-09 | 2025-12-30 | 12 | 17.9 | 0 |  | 3583 |  | N
700380 | 100401 | Corrective work on PP-GEN-01 | Corrective | P3 | Complete | Mechanical | 2025-12-06 | 2026-01-05 | 2025-12-19 | 2025-12-11 | 16 | 16.2 | 0 |  | 2923 |  | N
700381 | 100602 | Corrective work on HV-02 | Corrective | P3 | Complete | Fleet | 2025-12-05 | 2026-01-04 | 2025-12-07 | 2025-12-23 | 32 | 29.3 | 0 |  | 3257 |  | N
700382 | 100106 | Emergency work on AP-P-102 | Emergency | P1 | Complete | Mechanical | 2026-01-12 | 2026-01-19 | 2026-01-17 | 2026-02-04 | 40 | 49 | 0 |  | 3004 |  | N
700383 | 100108 | Corrective work on AP-P-201 | Corrective | P3 | Complete | Mechanical | 2026-01-12 | 2026-02-11 | 2026-01-17 | 2026-01-21 | 32 | 31.3 | 0 |  | 2777 |  | N
700384 | 100109 | Corrective work on AP-P-202 | Corrective | P2 | Complete | Mechanical | 2026-01-16 | 2026-02-15 | 2026-01-30 | 2026-01-25 | 24 | 25.7 | 0 |  | 5759 |  | N
700385 | 100105 | Corrective work on AP-P-101 | Corrective | P3 | Ready | Mechanical | 2026-01-20 | 2026-02-19 | 2026-01-21 |  | 8 |  | 0 |  |  | Y | N
700386 | 100114 | Corrective work on AP-PL-01 | Corrective | P3 | Scheduled | Boilermaker | 2026-01-25 | 2026-02-24 | 2026-02-05 |  | 8 |  | 0 |  |  | Y | N
700387 | 100112 | Emergency work on AP-CT-01 | Emergency | P1 | Ready | Mechanical | 2026-01-12 | 2026-01-19 | 2026-01-22 |  | 24 |  | 0 |  |  | Y | N
700388 | 100108 | Improvement work on AP-P-201 | Improvement | P2 | Complete | Mechanical | 2026-01-03 | 2026-02-02 | 2026-01-08 | 2026-01-25 | 32 | 45.8 | 0 |  | 2535 |  | N
700389 | 100401 | Corrective work on PP-GEN-01 | Corrective | P2 | Complete | Mechanical | 2026-01-04 | 2026-02-03 | 2026-01-05 | 2026-01-16 | 40 | 58.6 | 0 |  | 7545 |  | N
700390 | 100103 | Corrective work on AP-BL-01 | Corrective | P2 | Complete | Mechanical | 2026-01-05 | 2026-02-04 | 2026-01-12 | 2026-01-27 | 40 | 46.8 | 0 |  | 3612 |  | N
700391 | 100103 | Emergency work on AP-BL-01 | Emergency | P1 | Complete | Mechanical | 2026-01-17 | 2026-01-24 | 2026-01-19 | 2026-01-24 | 32 | 34.9 | 2 |  | 3280 |  | N
700392 | 100103 | Corrective work on AP-BL-01 | Corrective | P2 | Complete | Mechanical | 2026-01-23 | 2026-02-22 | 2026-01-28 | 2026-02-10 | 4 | 3.9 | 0 |  | 2097 |  | N
700393 | 100501 | Improvement work on LV-01 | Improvement | P3 | Open | Fleet | 2026-01-09 | 2026-02-08 | 2026-01-22 |  | 40 |  | 0 |  |  |  | N
700394 | 100101 | Corrective work on AP-SF-01 | Corrective | P3 | Complete | Boilermaker | 2026-01-20 | 2026-02-19 | 2026-01-23 | 2026-02-11 | 24 | 20.7 | 0 |  | 5553 |  | N
700395 | 100106 | Corrective work on AP-P-102 | Corrective | P3 | Complete | Mechanical | 2026-01-02 | 2026-02-01 | 2026-01-03 | 2026-01-12 | 4 | 3.6 | 0 |  | 1826 |  | N
700396 | 100501 | Corrective work on LV-01 | Corrective | P2 | Complete | Fleet | 2026-01-20 | 2026-02-19 | 2026-01-21 | 2026-02-14 | 32 | 33.9 | 0 |  | 3470 |  | N
700397 | 100113 | Corrective work on AP-TK-01 | Corrective | P2 | Complete | Boilermaker | 2026-01-08 | 2026-02-07 | 2026-01-21 | 2026-01-20 | 16 | 15.5 | 0 |  | 1291 |  | N
700398 | 100401 | Corrective work on PP-GEN-01 | Corrective | P3 | Complete | Mechanical | 2026-01-12 | 2026-02-11 | 2026-01-23 | 2026-02-03 | 12 | 11.6 | 0 |  | 4093 |  | N
700399 | 100106 | Corrective work on AP-P-102 | Corrective | P3 | Complete | Mechanical | 2026-01-07 | 2026-02-06 | 2026-01-10 | 2026-01-23 | 8 | 7.7 | 0 |  | 5860 |  | N
700400 | 100402 | Corrective work on PP-GEN-02 | Corrective | P2 | Complete | Mechanical | 2026-01-09 | 2026-02-08 | 2026-01-14 | 2026-01-28 | 4 | 3.9 | 0 |  | 2769 |  | N
700401 | 100111 | Emergency work on AP-AG-01 | Emergency | P1 | Complete | Mechanical | 2026-02-24 | 2026-03-03 | 2026-02-26 | 2026-03-04 | 24 | 20.5 | 4 |  | 3302 |  | N
700402 | 100115 | Corrective work on AP-AR-01 | Corrective | P3 | Complete | Boilermaker | 2026-02-07 | 2026-03-09 | 2026-02-09 | 2026-02-12 | 12 | 17.3 | 0 |  | 3871 |  | N
700403 | 100105 | Emergency work on AP-P-101 | Emergency | P1 | Open | Mechanical | 2026-02-14 | 2026-02-21 | 2026-02-21 |  | 12 |  | 0 |  |  |  | N
700404 | 100302 | Shutdown work on SS-MCC-01 | Shutdown | P3 | Complete | Electrical | 2026-02-19 | 2026-03-21 | 2026-02-20 | 2026-02-20 | 24 | 25.6 | 0 |  | 1833 |  | Y
700405 | 100114 | Corrective work on AP-PL-01 | Corrective | P3 | Complete | Boilermaker | 2026-02-06 | 2026-03-08 | 2026-02-12 | 2026-02-22 | 8 | 7.2 | 0 |  | 1616 |  | N
700406 | 100105 | Emergency work on AP-P-101 | Emergency | P1 | Open | Mechanical | 2026-02-26 | 2026-03-05 | 2026-03-01 |  | 8 |  | 0 |  |  |  | N
700407 | 100502 | Corrective work on LV-02 | Corrective | P2 | Complete | Fleet | 2026-02-22 | 2026-03-24 | 2026-03-08 | 2026-02-26 | 12 | 10.2 | 0 |  | 2214 |  | N
700408 | 100502 | Emergency work on LV-02 | Emergency | P1 | Complete | Fleet | 2026-02-12 | 2026-02-19 | 2026-02-22 | 2026-02-23 | 8 | 7.1 | 4 |  | 4776 |  | N
700409 | 100302 | Corrective work on SS-MCC-01 | Corrective | P2 | Open | Electrical | 2026-02-19 | 2026-03-21 | 2026-03-02 |  | 12 |  | 0 |  |  |  | N
700410 | 100108 | Corrective work on AP-P-201 | Corrective | P2 | Complete | Mechanical | 2026-02-01 | 2026-03-03 | 2026-02-04 | 2026-02-26 | 32 | 47.2 | 0 |  | 6928 |  | N
700411 | 100401 | Corrective work on PP-GEN-01 | Corrective | P3 | Scheduled | Mechanical | 2026-02-04 | 2026-03-06 | 2026-02-14 |  | 24 |  | 0 |  |  | Y | N
700412 | 100201 | Corrective work on CK-1080 | Corrective | P2 | Complete | Mechanical | 2026-02-15 | 2026-03-17 | 2026-02-23 | 2026-03-03 | 32 | 42.7 | 0 |  | 4981 |  | N
700413 | 100302 | Corrective work on SS-MCC-01 | Corrective | P2 | Complete | Electrical | 2026-02-02 | 2026-03-04 | 2026-02-03 | 2026-02-15 | 32 | 26.1 | 0 |  | 5173 |  | N
700414 | 100602 | Corrective work on HV-02 | Corrective | P3 | Complete | Fleet | 2026-02-16 | 2026-03-18 | 2026-02-17 | 2026-02-17 | 8 | 7.3 | 0 |  | 840 |  | N
700415 | 100111 | Emergency work on AP-AG-01 | Emergency | P1 | Complete | Mechanical | 2026-02-09 | 2026-02-16 | 2026-02-14 | 2026-03-04 | 16 | 19.8 | 0 |  | 2262 |  | N
700416 | 100112 | Improvement work on AP-CT-01 | Improvement | P3 | Complete | Mechanical | 2026-02-05 | 2026-03-07 | 2026-02-10 | 2026-02-19 | 16 | 16.5 | 0 |  | 4926 |  | N
700417 | 100108 | Shutdown work on AP-P-201 | Shutdown | P3 | Open | Mechanical | 2026-02-22 | 2026-03-24 | 2026-03-03 |  | 72 |  | 0 |  |  |  | Y
700418 | 100302 | Emergency work on SS-MCC-01 | Emergency | P1 | Open | Electrical | 2026-02-10 | 2026-02-17 | 2026-02-19 |  | 12 |  | 4 |  |  |  | N
700419 | 100113 | Emergency work on AP-TK-01 | Emergency | P1 | Complete | Boilermaker | 2026-02-06 | 2026-02-13 | 2026-02-17 | 2026-02-27 | 4 | 5.1 | 0 |  | 4227 |  | N
700420 | 100104 | Emergency work on AP-CV-01 | Emergency | P1 | Scheduled | Boilermaker | 2026-03-16 | 2026-03-23 | 2026-03-27 |  | 32 |  | 0 |  |  | Y | N
700421 | 100404 | Corrective work on PP-GEN-04 | Corrective | P3 | Complete | Mechanical | 2026-03-16 | 2026-04-15 | 2026-03-17 | 2026-04-06 | 24 | 20.7 | 0 |  | 5375 |  | N
700422 | 100403 | Corrective work on PP-GEN-03 | Corrective | P3 | Complete | Mechanical | 2026-03-16 | 2026-04-15 | 2026-03-17 | 2026-03-17 | 12 | 10.3 | 0 |  | 1114 |  | N
700423 | 100108 | Emergency work on AP-P-201 | Emergency | P1 | Open | Mechanical | 2026-03-19 | 2026-03-26 | 2026-03-30 |  | 12 |  | 4 |  |  |  | N
700424 | 100104 | Corrective work on AP-CV-01 | Corrective | P3 | Complete | Boilermaker | 2026-03-14 | 2026-04-13 | 2026-03-17 | 2026-03-17 | 16 | 16.1 | 0 |  | 6353 |  | N
700425 | 100301 | Corrective work on SS-TX-01 | Corrective | P3 | Complete | Electrical | 2026-03-17 | 2026-04-16 | 2026-03-30 | 2026-03-24 | 32 | 32.3 | 0 |  | 7171 |  | N
700426 | 100105 | Corrective work on AP-P-101 | Corrective | P2 | Ready | Mechanical | 2026-03-22 | 2026-04-21 | 2026-03-24 |  | 12 |  | 0 |  |  | Y | N
700427 | 100603 | Corrective work on HV-03 | Corrective | P3 | Complete | Fleet | 2026-03-16 | 2026-04-15 | 2026-03-24 | 2026-03-17 | 24 | 32.5 | 0 |  | 6301 |  | N
700428 | 100404 | Improvement work on PP-GEN-04 | Improvement | P2 | Complete | Mechanical | 2026-03-13 | 2026-04-12 | 2026-03-15 | 2026-03-16 | 32 | 31.4 | 0 |  | 4059 |  | N
700429 | 100113 | Corrective work on AP-TK-01 | Corrective | P3 | Complete | Boilermaker | 2026-03-10 | 2026-04-09 | 2026-03-22 | 2026-04-04 | 40 | 49.4 | 0 |  | 3126 |  | N
700430 | 100502 | Corrective work on LV-02 | Corrective | P3 | Complete | Fleet | 2026-03-24 | 2026-04-23 | 2026-04-06 | 2026-04-07 | 40 | 53.1 | 0 |  | 2120 |  | N
700431 | 100401 | Improvement work on PP-GEN-01 | Improvement | P3 | Complete | Mechanical | 2026-03-09 | 2026-04-08 | 2026-03-21 | 2026-03-25 | 8 | 8.4 | 0 |  | 687 |  | N
700432 | 100106 | Emergency work on AP-P-102 | Emergency | P1 | Complete | Mechanical | 2026-03-16 | 2026-03-23 | 2026-03-29 | 2026-04-06 | 24 | 21.2 | 0 |  | 5525 |  | N
700433 | 100114 | Corrective work on AP-PL-01 | Corrective | P3 | Complete | Boilermaker | 2026-03-11 | 2026-04-10 | 2026-03-22 | 2026-03-12 | 32 | 42.9 | 0 |  | 2545 |  | N
700434 | 100111 | Improvement work on AP-AG-01 | Improvement | P3 | Ready | Mechanical | 2026-03-11 | 2026-04-10 | 2026-03-24 |  | 12 |  | 0 |  |  | Y | N
700435 | 100102 | Corrective work on AP-WHB-01 | Corrective | P2 | Complete | Boilermaker | 2026-03-11 | 2026-04-10 | 2026-03-13 | 2026-03-27 | 4 | 5.6 | 0 |  | 4686 |  | N
700436 | 100102 | Emergency work on AP-WHB-01 | Emergency | P1 | Complete | Boilermaker | 2026-03-16 | 2026-03-23 | 2026-03-26 | 2026-03-26 | 8 | 8.4 | 2 |  | 3182 |  | N
700437 | 100113 | Corrective work on AP-TK-01 | Corrective | P2 | Scheduled | Boilermaker | 2026-03-03 | 2026-04-02 | 2026-03-10 |  | 12 |  | 0 |  |  | Y | N
700438 | 100108 | Corrective work on AP-P-201 | Corrective | P3 | Scheduled | Mechanical | 2026-03-26 | 2026-04-25 | 2026-04-03 |  | 4 |  | 0 |  |  | Y | N
700439 | 100114 | Corrective work on AP-PL-01 | Corrective | P3 | Ready | Boilermaker | 2026-04-25 | 2026-05-25 | 2026-04-26 |  | 24 |  | 0 |  |  | Y | N
700440 | 100301 | Corrective work on SS-TX-01 | Corrective | P2 | Open | Electrical | 2026-04-03 | 2026-05-03 | 2026-04-12 |  | 4 |  | 0 |  |  |  | N
700441 | 100109 | Emergency work on AP-P-202 | Emergency | P1 | Complete | Mechanical | 2026-04-26 | 2026-05-03 | 2026-05-09 | 2026-05-07 | 12 | 16.3 | 0 |  | 6483 |  | N
700442 | 100102 | Corrective work on AP-WHB-01 | Corrective | P3 | Open | Boilermaker | 2026-04-15 | 2026-05-15 | 2026-04-16 |  | 16 |  | 0 |  |  |  | N
700443 | 100302 | Corrective work on SS-MCC-01 | Corrective | P2 | Complete | Electrical | 2026-04-03 | 2026-05-03 | 2026-04-10 | 2026-04-23 | 16 | 18.4 | 0 |  | 2905 |  | N
700444 | 100113 | Corrective work on AP-TK-01 | Corrective | P2 | Open | Boilermaker | 2026-04-21 | 2026-05-21 | 2026-05-03 |  | 16 |  | 0 |  |  |  | N
700445 | 100401 | Corrective work on PP-GEN-01 | Corrective | P3 | Complete | Mechanical | 2026-04-05 | 2026-05-05 | 2026-04-07 | 2026-04-18 | 4 | 5.3 | 0 |  | 4138 |  | N
700446 | 100402 | Corrective work on PP-GEN-02 | Corrective | P3 | Complete | Mechanical | 2026-04-04 | 2026-05-04 | 2026-04-15 | 2026-04-28 | 16 | 14.1 | 0 |  | 3391 |  | N
700447 | 100101 | Emergency work on AP-SF-01 | Emergency | P1 | Complete | Boilermaker | 2026-04-08 | 2026-04-15 | 2026-04-20 | 2026-04-27 | 16 | 17.3 | 0 |  | 3008 |  | N
700448 | 100102 | Corrective work on AP-WHB-01 | Corrective | P3 | Complete | Boilermaker | 2026-04-26 | 2026-05-26 | 2026-04-30 | 2026-05-03 | 12 | 13.4 | 0 |  | 3284 |  | N
700449 | 100107 | Corrective work on AP-P-103 | Corrective | P3 | Open | Mechanical | 2026-04-20 | 2026-05-20 | 2026-05-02 |  | 24 |  | 0 |  |  |  | N
700450 | 100201 | Emergency work on CK-1080 | Emergency | P1 | Complete | Mechanical | 2026-04-21 | 2026-04-28 | 2026-04-30 | 2026-05-04 | 32 | 47.5 | 2 |  | 7198 |  | N
700451 | 100103 | Corrective work on AP-BL-01 | Corrective | P3 | Complete | Mechanical | 2026-04-24 | 2026-05-24 | 2026-05-01 | 2026-05-14 | 24 | 22.8 | 0 |  | 3744 |  | N
700452 | 100108 | Emergency work on AP-P-201 | Emergency | P1 | Complete | Mechanical | 2026-04-20 | 2026-04-27 | 2026-04-30 | 2026-05-14 | 12 | 15.6 | 0 |  | 4108 |  | N
700453 | 100112 | Corrective work on AP-CT-01 | Corrective | P3 | Complete | Mechanical | 2026-04-25 | 2026-05-25 | 2026-04-30 | 2026-05-08 | 8 | 12 | 0 |  | 2110 |  | N
700454 | 100502 | Corrective work on LV-02 | Corrective | P3 | Complete | Fleet | 2026-04-14 | 2026-05-14 | 2026-04-16 | 2026-04-21 | 40 | 48.5 | 0 |  | 7933 |  | N
700455 | 100501 | Corrective work on LV-01 | Corrective | P3 | Complete | Fleet | 2026-04-25 | 2026-05-25 | 2026-05-07 | 2026-05-11 | 12 | 15.3 | 0 |  | 4039 |  | N
700456 | 100302 | Shutdown work on SS-MCC-01 | Shutdown | P3 | Complete | Electrical | 2026-04-06 | 2026-05-06 | 2026-04-19 | 2026-05-01 | 72 | 94.2 | 0 |  | 3876 |  | Y
700457 | 100109 | Corrective work on AP-P-202 | Corrective | P2 | Complete | Mechanical | 2026-04-25 | 2026-05-25 | 2026-05-06 | 2026-05-11 | 12 | 16.3 | 0 |  | 4750 |  | N
700458 | 100404 | Corrective work on PP-GEN-04 | Corrective | P2 | Open | Mechanical | 2026-04-16 | 2026-05-16 | 2026-04-26 |  | 16 |  | 0 |  |  |  | N
700459 | 100115 | Corrective work on AP-AR-01 | Corrective | P3 | Open | Boilermaker | 2026-05-15 | 2026-06-14 | 2026-05-21 |  | 24 |  | 0 |  |  |  | N
700460 | 100114 | Corrective work on AP-PL-01 | Corrective | P2 | Complete | Boilermaker | 2026-05-25 | 2026-06-24 | 2026-06-06 | 2026-06-12 | 32 | 33.7 | 0 |  | 3469 |  | N
700461 | 100113 | Corrective work on AP-TK-01 | Corrective | P2 | Complete | Boilermaker | 2026-05-23 | 2026-06-22 | 2026-06-01 | 2026-06-10 | 24 | 25.5 | 0 |  | 6684 |  | N
700462 | 100113 | Emergency work on AP-TK-01 | Emergency | P1 | Complete | Boilermaker | 2026-05-05 | 2026-05-12 | 2026-05-09 | 2026-05-25 | 8 | 7.4 | 0 |  | 1202 |  | N
700463 | 100403 | Corrective work on PP-GEN-03 | Corrective | P2 | Complete | Mechanical | 2026-05-26 | 2026-06-25 | 2026-06-07 | 2026-05-27 | 16 | 19.3 | 0 |  | 6352 |  | N
700464 | 100603 | Emergency work on HV-03 | Emergency | P1 | Complete | Fleet | 2026-05-10 | 2026-05-17 | 2026-05-22 | 2026-06-02 | 12 | 12.3 | 0 |  | 4582 |  | N
700465 | 100501 | Corrective work on LV-01 | Corrective | P3 | Ready | Fleet | 2026-05-11 | 2026-06-10 | 2026-05-15 |  | 40 |  | 0 |  |  | Y | N
700466 | 100302 | Corrective work on SS-MCC-01 | Corrective | P3 | Complete | Electrical | 2026-05-08 | 2026-06-07 | 2026-05-15 | 2026-05-29 | 12 | 11.1 | 0 |  | 2193 |  | N
700467 | 100401 | Emergency work on PP-GEN-01 | Emergency | P1 | Complete | Mechanical | 2026-05-22 | 2026-05-29 | 2026-05-28 | 2026-06-11 | 32 | 30.4 | 0 |  | 3555 |  | N
700468 | 100201 | Corrective work on CK-1080 | Corrective | P2 | Complete | Mechanical | 2026-05-12 | 2026-06-11 | 2026-05-25 | 2026-06-03 | 4 | 5.6 | 0 |  | 4750 |  | N
700469 | 100401 | Corrective work on PP-GEN-01 | Corrective | P3 | Complete | Mechanical | 2026-05-01 | 2026-05-31 | 2026-05-11 | 2026-05-13 | 40 | 46.9 | 0 |  | 5266 |  | N
700470 | 100103 | Corrective work on AP-BL-01 | Corrective | P2 | Complete | Mechanical | 2026-05-26 | 2026-06-25 | 2026-06-04 | 2026-06-18 | 24 | 23.8 | 0 |  | 6764 |  | N
700471 | 100105 | Corrective work on AP-P-101 | Corrective | P2 | Complete | Mechanical | 2026-05-23 | 2026-06-22 | 2026-06-01 | 2026-06-17 | 12 | 9.8 | 0 |  | 2745 |  | N
700472 | 100112 | Corrective work on AP-CT-01 | Corrective | P2 | Complete | Mechanical | 2026-05-01 | 2026-05-31 | 2026-05-07 | 2026-05-10 | 4 | 4.1 | 0 |  | 5149 |  | N
700473 | 100106 | Corrective work on AP-P-102 | Corrective | P2 | Complete | Mechanical | 2026-05-09 | 2026-06-08 | 2026-05-14 | 2026-05-13 | 16 | 18.9 | 0 |  | 6000 |  | N
700474 | 100404 | Corrective work on PP-GEN-04 | Corrective | P3 | Complete | Mechanical | 2026-06-15 | 2026-07-15 | 2026-06-21 | 2026-06-29 | 40 | 46.1 | 0 |  | 5938 |  | N
700475 | 100115 | Corrective work on AP-AR-01 | Corrective | P3 | Open | Boilermaker | 2026-06-17 | 2026-07-17 | 2026-06-18 |  | 40 |  | 0 |  |  |  | N
700476 | 100110 | Corrective work on AP-P-301 | Corrective | P3 | Complete | Mechanical | 2026-06-10 | 2026-07-10 | 2026-06-15 | 2026-06-12 | 24 | 28 | 0 |  | 4310 |  | N
700477 | 100603 | Corrective work on HV-03 | Corrective | P2 | Complete | Fleet | 2026-06-18 | 2026-07-18 | 2026-06-25 | 2026-07-12 | 16 | 18.4 | 0 |  | 2756 |  | N
700478 | 100401 | Improvement work on PP-GEN-01 | Improvement | P2 | Open | Mechanical | 2026-06-21 | 2026-07-21 | 2026-06-30 |  | 4 |  | 0 |  |  |  | N
700479 | 100111 | Corrective work on AP-AG-01 | Corrective | P3 | Complete | Mechanical | 2026-06-18 | 2026-07-18 | 2026-06-27 | 2026-06-20 | 40 | 42 | 0 |  | 2718 |  | N
700480 | 100302 | Corrective work on SS-MCC-01 | Corrective | P2 | Complete | Electrical | 2026-06-04 | 2026-07-04 | 2026-06-12 | 2026-06-17 | 32 | 38.2 | 0 |  | 5267 |  | N
700481 | 100401 | Corrective work on PP-GEN-01 | Corrective | P2 | Complete | Mechanical | 2026-06-25 | 2026-07-25 | 2026-07-03 | 2026-07-18 | 8 | 10.6 | 0 |  | 2484 |  | N
700482 | 100404 | Corrective work on PP-GEN-04 | Corrective | P3 | Complete | Mechanical | 2026-06-16 | 2026-07-16 | 2026-06-26 | 2026-07-04 | 40 | 57.8 | 0 |  | 7135 |  | N
700483 | 100101 | Corrective work on AP-SF-01 | Corrective | P2 | Complete | Boilermaker | 2026-06-01 | 2026-07-01 | 2026-06-05 | 2026-06-08 | 24 | 32 | 0 |  | 4035 |  | N
700484 | 100106 | Corrective work on AP-P-102 | Corrective | P2 | Ready | Mechanical | 2026-06-18 | 2026-07-18 | 2026-07-02 |  | 8 |  | 0 |  |  | Y | N
700485 | 100602 | Corrective work on HV-02 | Corrective | P2 | Complete | Fleet | 2026-06-24 | 2026-07-24 | 2026-07-07 | 2026-07-06 | 4 | 3.8 | 0 |  | 545 |  | N
700486 | 100502 | Emergency work on LV-02 | Emergency | P1 | Complete | Fleet | 2026-06-06 | 2026-06-13 | 2026-06-11 | 2026-06-17 | 40 | 57.2 | 0 |  | 4717 |  | N
700487 | 100403 | Corrective work on PP-GEN-03 | Corrective | P3 | Ready | Mechanical | 2026-06-04 | 2026-07-04 | 2026-06-18 |  | 4 |  | 0 |  |  | Y | N
700488 | 100404 | Corrective work on PP-GEN-04 | Corrective | P2 | Complete | Mechanical | 2026-06-09 | 2026-07-09 | 2026-06-13 | 2026-06-23 | 16 | 19.4 | 0 |  | 3115 |  | N
700489 | 100107 | Corrective work on AP-P-103 | Corrective | P3 | Complete | Mechanical | 2026-06-22 | 2026-07-22 | 2026-06-27 | 2026-07-15 | 8 | 11.6 | 0 |  | 5950 |  | N
700490 | 100501 | Improvement work on LV-01 | Improvement | P3 | Complete | Fleet | 2026-06-04 | 2026-07-04 | 2026-06-16 | 2026-06-25 | 32 | 32.8 | 0 |  | 1757 |  | N
700491 | 100102 | Corrective work on AP-WHB-01 | Corrective | P2 | Complete | Boilermaker | 2026-06-14 | 2026-07-14 | 2026-06-16 | 2026-07-01 | 12 | 9.8 | 0 |  | 5689 |  | N
700492 | 100112 | Corrective work on AP-CT-01 | Corrective | P2 | Complete | Mechanical | 2026-06-18 | 2026-07-18 | 2026-06-22 | 2026-07-07 | 32 | 36.8 | 0 |  | 5793 |  | N
700493 | 100404 | Corrective work on PP-GEN-04 | Corrective | P3 | Complete | Mechanical | 2026-06-25 | 2026-07-25 | 2026-07-07 | 2026-07-10 | 8 | 6.6 | 0 |  | 4945 |  | N
700494 | 100102 | Corrective work on AP-WHB-01 | Corrective | P3 | Complete | Boilermaker | 2026-06-05 | 2026-07-05 | 2026-06-17 | 2026-06-19 | 24 | 21.9 | 0 |  | 4281 |  | N
700495 | 100102 | Emergency work on AP-WHB-01 | Emergency | P1 | Complete | Boilermaker | 2026-07-12 | 2026-07-19 | 2026-07-13 | 2026-07-18 | 24 | 34.3 | 0 |  | 6601 |  | N
700496 | 100113 | Corrective work on AP-TK-01 | Corrective | P2 | Complete | Boilermaker | 2026-07-05 | 2026-08-04 | 2026-07-15 | 2026-07-16 | 24 | 21.1 | 0 |  | 3648 |  | N
700497 | 100106 | Corrective work on AP-P-102 | Corrective | P2 | Complete | Mechanical | 2026-07-07 | 2026-08-06 | 2026-07-09 | 2026-07-10 | 32 | 29.4 | 0 |  | 6087 |  | N
700498 | 100602 | Corrective work on HV-02 | Corrective | P2 | Complete | Fleet | 2026-07-13 | 2026-08-12 | 2026-07-20 | 2026-08-06 | 24 | 19.3 | 0 |  | 3818 |  | N
700499 | 100102 | Corrective work on AP-WHB-01 | Corrective | P3 | Scheduled | Boilermaker | 2026-07-20 | 2026-08-19 | 2026-07-25 |  | 4 |  | 0 |  |  | Y | N
700500 | 100302 | Improvement work on SS-MCC-01 | Improvement | P3 | Complete | Electrical | 2026-07-10 | 2026-08-09 | 2026-07-22 | 2026-07-23 | 40 | 35 | 0 |  | 7449 |  | N
700501 | 100102 | Corrective work on AP-WHB-01 | Corrective | P2 | Complete | Boilermaker | 2026-07-09 | 2026-08-08 | 2026-07-21 | 2026-08-03 | 40 | 52.5 | 0 |  | 7366 |  | N
700502 | 100106 | Corrective work on AP-P-102 | Corrective | P2 | Ready | Mechanical | 2026-07-21 | 2026-08-20 | 2026-07-30 |  | 40 |  | 0 |  |  | Y | N
700503 | 100104 | Corrective work on AP-CV-01 | Corrective | P3 | Complete | Boilermaker | 2026-07-24 | 2026-08-23 | 2026-07-28 | 2026-08-12 | 24 | 33.3 | 0 |  | 6672 |  | N
700504 | 100109 | Corrective work on AP-P-202 | Corrective | P2 | Complete | Mechanical | 2026-07-19 | 2026-08-18 | 2026-08-01 | 2026-08-07 | 4 | 5.4 | 0 |  | 809 |  | N
700505 | 100114 | Corrective work on AP-PL-01 | Corrective | P2 | Complete | Boilermaker | 2026-07-21 | 2026-08-20 | 2026-07-26 | 2026-08-10 | 16 | 17.8 | 0 |  | 1147 |  | N
700506 | 100109 | Corrective work on AP-P-202 | Corrective | P3 | Complete | Mechanical | 2026-07-06 | 2026-08-05 | 2026-07-10 | 2026-07-13 | 24 | 25.6 | 0 |  | 6278 |  | N
700507 | 100111 | Corrective work on AP-AG-01 | Corrective | P3 | Complete | Mechanical | 2026-07-24 | 2026-08-23 | 2026-08-04 | 2026-07-25 | 32 | 31.8 | 0 |  | 5853 |  | N
700508 | 100403 | Corrective work on PP-GEN-03 | Corrective | P3 | Complete | Mechanical | 2026-07-01 | 2026-07-31 | 2026-07-04 | 2026-07-09 | 40 | 52.2 | 0 |  | 5984 |  | N
700509 | 100404 | Corrective work on PP-GEN-04 | Corrective | P3 | Complete | Mechanical | 2026-07-14 | 2026-08-13 | 2026-07-23 | 2026-07-22 | 12 | 15.4 | 0 |  | 1944 |  | N
700510 | 100602 | Improvement work on HV-02 | Improvement | P2 | Complete | Fleet | 2026-07-21 | 2026-08-20 | 2026-08-01 | 2026-08-10 | 24 | 19.8 | 0 |  | 4691 |  | N
700511 | 100106 | Corrective work on AP-P-102 | Corrective | P2 | Complete | Mechanical | 2026-07-18 | 2026-08-17 | 2026-07-24 | 2026-08-09 | 12 | 10.4 | 0 |  | 992 |  | N
700512 | 100105 | Corrective work on AP-P-101 | Corrective | P3 | Complete | Mechanical | 2026-07-15 | 2026-08-14 | 2026-07-29 | 2026-07-24 | 24 | 33.3 | 0 |  | 2225 |  | N
700513 | 100102 | Corrective work on AP-WHB-01 | Corrective | P2 | Complete | Boilermaker | 2026-07-21 | 2026-08-20 | 2026-08-04 | 2026-07-25 | 4 | 3.4 | 0 |  | 4654 |  | N
700514 | 100112 | Corrective work on AP-CT-01 | Corrective | P3 | Complete | Mechanical | 2026-07-05 | 2026-08-04 | 2026-07-16 | 2026-07-17 | 4 | 5 | 0 |  | 3342 |  | N
700515 | 100302 | Corrective work on SS-MCC-01 | Corrective | P3 | Ready | Electrical | 2026-08-21 | 2026-09-20 | 2026-08-29 |  | 32 |  | 0 |  |  | Y | N
700516 | 100601 | Corrective work on HV-01 | Corrective | P3 | Complete | Fleet | 2026-08-10 | 2026-09-09 | 2026-08-24 | 2026-08-11 | 16 | 15.7 | 0 |  | 5827 |  | N
700517 | 100301 | Corrective work on SS-TX-01 | Corrective | P3 | Complete | Electrical | 2026-08-06 | 2026-09-05 | 2026-08-17 | 2026-08-11 | 12 | 10.4 | 0 |  | 3076 |  | N
700518 | 100103 | Corrective work on AP-BL-01 | Corrective | P3 | Complete | Mechanical | 2026-08-15 | 2026-09-14 | 2026-08-22 | 2026-08-24 | 16 | 20.4 | 0 |  | 3827 |  | N
700519 | 100103 | Corrective work on AP-BL-01 | Corrective | P2 | Complete | Mechanical | 2026-08-04 | 2026-09-03 | 2026-08-12 | 2026-08-07 | 32 | 28.9 | 0 |  | 5168 |  | N
700520 | 100104 | Corrective work on AP-CV-01 | Corrective | P3 | Complete | Boilermaker | 2026-08-20 | 2026-09-19 | 2026-08-26 | 2026-09-10 | 12 | 12.8 | 0 |  | 2446 |  | N
700521 | 100502 | Corrective work on LV-02 | Corrective | P2 | Complete | Fleet | 2026-08-01 | 2026-08-31 | 2026-08-04 | 2026-08-06 | 8 | 7 | 0 |  | 1027 |  | N
700522 | 100401 | Corrective work on PP-GEN-01 | Corrective | P2 | Complete | Mechanical | 2026-08-22 | 2026-09-21 | 2026-08-27 | 2026-08-28 | 24 | 34.9 | 0 |  | 4045 |  | N
700523 | 100501 | Corrective work on LV-01 | Corrective | P3 | Complete | Fleet | 2026-08-05 | 2026-09-04 | 2026-08-13 | 2026-08-23 | 4 | 4.3 | 0 |  | 1991 |  | N
700524 | 100603 | Improvement work on HV-03 | Improvement | P3 | Complete | Fleet | 2026-08-02 | 2026-09-01 | 2026-08-09 | 2026-08-18 | 12 | 11.4 | 0 |  | 5969 |  | N
700525 | 100103 | Improvement work on AP-BL-01 | Improvement | P3 | Open | Mechanical | 2026-08-14 | 2026-09-13 | 2026-08-15 |  | 24 |  | 0 |  |  |  | N
700526 | 100502 | Improvement work on LV-02 | Improvement | P2 | Open | Fleet | 2026-08-14 | 2026-09-13 | 2026-08-28 |  | 4 |  | 0 |  |  |  | N
700527 | 100302 | Shutdown work on SS-MCC-01 | Shutdown | P3 | Open | Electrical | 2026-08-17 | 2026-09-16 | 2026-08-31 |  | 24 |  | 0 |  |  |  | Y
700528 | 100106 | Emergency work on AP-P-102 | Emergency | P1 | Complete | Mechanical | 2026-08-20 | 2026-08-27 | 2026-08-27 | 2026-08-31 | 32 | 45.1 | 0 |  | 5497 |  | N
700529 | 100103 | Corrective work on AP-BL-01 | Corrective | P3 | Complete | Mechanical | 2026-08-04 | 2026-09-03 | 2026-08-12 | 2026-08-12 | 40 | 55.7 | 0 |  | 6080 |  | N
700530 | 100112 | Corrective work on AP-CT-01 | Corrective | P2 | Complete | Mechanical | 2026-08-07 | 2026-09-06 | 2026-08-10 | 2026-08-27 | 24 | 20.7 | 0 |  | 5441 |  | N
700531 | 100402 | Corrective work on PP-GEN-02 | Corrective | P3 | Complete | Mechanical | 2026-08-17 | 2026-09-16 | 2026-08-24 | 2026-09-06 | 40 | 38.6 | 0 |  | 5166 |  | N
700532 | 100114 | Corrective work on AP-PL-01 | Corrective | P3 | Complete | Boilermaker | 2026-08-26 | 2026-09-25 | 2026-09-04 | 2026-09-07 | 16 | 22.3 | 0 |  | 6539 |  | N
700533 | 100105 | Corrective work on AP-P-101 | Corrective | P3 | Scheduled | Mechanical | 2026-09-10 | 2026-10-10 | 2026-09-20 |  | 12 |  | 0 |  |  | Y | N
700534 | 100104 | Corrective work on AP-CV-01 | Corrective | P2 | Scheduled | Boilermaker | 2026-09-26 | 2026-10-26 | 2026-10-08 |  | 24 |  | 0 |  |  | Y | N
700535 | 100105 | Corrective work on AP-P-101 | Corrective | P3 | Ready | Mechanical | 2026-09-21 | 2026-10-21 | 2026-09-25 |  | 24 |  | 0 |  |  | Y | N
700536 | 100104 | Corrective work on AP-CV-01 | Corrective | P3 | Ready | Boilermaker | 2026-09-03 | 2026-10-03 | 2026-09-16 |  | 8 |  | 0 |  |  | Y | N
700537 | 100109 | Corrective work on AP-P-202 | Corrective | P3 | Ready | Mechanical | 2026-09-10 | 2026-10-10 | 2026-09-14 |  | 24 |  | 0 |  |  | Y | N
700538 | 100101 | Corrective work on AP-SF-01 | Corrective | P2 | Complete | Boilermaker | 2026-09-04 | 2026-10-04 | 2026-09-08 | 2026-09-28 | 24 | 26.8 | 0 |  | 6204 |  | N
700539 | 100201 | Corrective work on CK-1080 | Corrective | P3 | Ready | Mechanical | 2026-09-11 | 2026-10-11 | 2026-09-14 |  | 16 |  | 0 |  |  | Y | N
700540 | 100112 | Improvement work on AP-CT-01 | Improvement | P2 | Open | Mechanical | 2026-09-20 | 2026-10-20 | 2026-09-26 |  | 24 |  | 0 |  |  |  | N
700541 | 100602 | Corrective work on HV-02 | Corrective | P2 | Open | Fleet | 2026-09-21 | 2026-10-21 | 2026-09-28 |  | 4 |  | 0 |  |  |  | N
700542 | 100402 | Corrective work on PP-GEN-02 | Corrective | P2 | Complete | Mechanical | 2026-09-06 | 2026-10-06 | 2026-09-19 | 2026-09-16 | 12 | 13.4 | 0 |  | 993 |  | N
700543 | 100201 | Emergency work on CK-1080 | Emergency | P1 | Scheduled | Mechanical | 2026-09-05 | 2026-09-12 | 2026-09-18 |  | 8 |  | 4 |  |  | Y | N
700544 | 100502 | Emergency work on LV-02 | Emergency | P1 | Scheduled | Fleet | 2026-09-23 | 2026-09-30 | 2026-09-25 |  | 40 |  | 0 |  |  | Y | N
700545 | 100502 | Emergency work on LV-02 | Emergency | P1 | Ready | Fleet | 2026-09-02 | 2026-09-09 | 2026-09-04 |  | 40 |  | 2 |  |  | Y | N
700546 | 100105 | Corrective work on AP-P-101 | Corrective | P2 | Ready | Mechanical | 2026-09-15 | 2026-10-15 | 2026-09-29 |  | 32 |  | 0 |  |  | Y | N
700547 | 100111 | Corrective work on AP-AG-01 | Corrective | P2 | Open | Mechanical | 2026-09-26 | 2026-10-26 | 2026-09-28 |  | 16 |  | 0 |  |  |  | N
700548 | 100112 | Corrective work on AP-CT-01 | Corrective | P3 | Open | Mechanical | 2026-09-09 | 2026-10-09 | 2026-09-15 |  | 40 |  | 0 |  |  |  | N
700549 | 100301 | Corrective work on SS-TX-01 | Corrective | P3 | Open | Electrical | 2026-09-21 | 2026-10-21 | 2026-09-23 |  | 12 |  | 0 |  |  |  | N
700550 | 100302 | Corrective work on SS-MCC-01 | Corrective | P2 | Scheduled | Electrical | 2026-09-05 | 2026-10-05 | 2026-09-09 |  | 24 |  | 0 |  |  | Y | N
700551 | 100603 | Corrective work on HV-03 | Corrective | P3 | Open | Fleet | 2026-09-21 | 2026-10-21 | 2026-10-01 |  | 16 |  | 0 |  |  |  | N
700552 | 100107 | Corrective work on AP-P-103 | Corrective | P2 | Complete | Mechanical | 2026-09-21 | 2026-10-21 | 2026-09-29 | 2026-09-29 | 4 | 5.6 | 0 |  | 3188 |  | N

## Production
AHIM Production and availability by circuit
One row per month and circuit. Circuit names must match the Area names in the Asset_Register. Source: Metallurgy / production report. Frequency: Monthly. Key: Month + Circuit.
Month | Circuit | Production unit | Planned hours | Operating hours | Maintenance downtime (h) | Process downtime (h) | Other downtime (h) | Production | Lost production value (USD)
2025-10-01 | Acid plant | t H2SO4 | 744 | 718.1 | 10.5 | 8.6 | 6.8 | 17661 | 9450
2025-10-01 | Calciner | kg U3O8 | 744 | 706.7 | 17.7 | 19.4 | 0.2 | 67654 | 44250
2025-10-01 | Power plant | MWh | 744 | 694.1 | 30.2 | 12.1 | 7.6 | 6710 | 12080
2025-11-01 | Acid plant | t H2SO4 | 720 | 668.4 | 35.2 | 15.2 | 1.2 | 16419 | 31680
2025-11-01 | Calciner | kg U3O8 | 720 | 672.9 | 23.8 | 18.9 | 4.4 | 65172 | 59500
2025-11-01 | Power plant | MWh | 720 | 682.9 | 26.7 | 7.6 | 2.8 | 6086 | 10680
2025-12-01 | Acid plant | t H2SO4 | 744 | 717.6 | 14.3 | 5.8 | 6.3 | 16790 | 12870
2025-12-01 | Calciner | kg U3O8 | 744 | 683.8 | 43.6 | 13.9 | 2.7 | 61611 | 109000
2025-12-01 | Power plant | MWh | 744 | 709.2 | 17.6 | 11.1 | 6.1 | 6391 | 7040
2026-01-01 | Acid plant | t H2SO4 | 744 | 680 | 43.3 | 19.1 | 1.6 | 16453 | 38970
2026-01-01 | Calciner | kg U3O8 | 744 | 702.3 | 29.6 | 5.4 | 6.7 | 62342 | 74000
2026-01-01 | Power plant | MWh | 744 | 707.4 | 30.4 | 5.4 | 0.8 | 6901 | 12160
2026-02-01 | Acid plant | t H2SO4 | 600 | 544.8 | 47.8 | 5 | 2.4 | 13134 | 43020
2026-02-01 | Calciner | kg U3O8 | 672 | 627.7 | 32 | 5.5 | 6.8 | 57419 | 80000
2026-02-01 | Power plant | MWh | 672 | 613 | 47.7 | 7.6 | 3.7 | 5942 | 19080
2026-03-01 | Acid plant | t H2SO4 | 744 | 717.9 | 10.1 | 13.4 | 2.6 | 16848 | 9090
2026-03-01 | Calciner | kg U3O8 | 744 | 707.1 | 19.6 | 17 | 0.3 | 64459 | 49000
2026-03-01 | Power plant | MWh | 744 | 690.3 | 33.6 | 16.9 | 3.2 | 6149 | 13440
2026-04-01 | Acid plant | t H2SO4 | 720 | 674.1 | 32 | 10.6 | 3.3 | 16353 | 28800
2026-04-01 | Calciner | kg U3O8 | 720 | 680.3 | 24.7 | 11 | 4 | 65113 | 61750
2026-04-01 | Power plant | MWh | 720 | 692.8 | 16.6 | 8.3 | 2.3 | 6730 | 6640
2026-05-01 | Acid plant | t H2SO4 | 744 | 707.4 | 23.1 | 9.9 | 3.6 | 16527 | 20790
2026-05-01 | Calciner | kg U3O8 | 744 | 702.3 | 24.3 | 16.7 | 0.7 | 66202 | 60750
2026-05-01 | Power plant | MWh | 744 | 718.4 | 8.2 | 16.1 | 1.3 | 6509 | 3280
2026-06-01 | Acid plant | t H2SO4 | 720 | 670.1 | 30.5 | 13.5 | 5.9 | 15628 | 27450
2026-06-01 | Calciner | kg U3O8 | 720 | 697.9 | 8.2 | 12.6 | 1.3 | 64439 | 20500
2026-06-01 | Power plant | MWh | 720 | 678.2 | 19.3 | 17.3 | 5.2 | 6054 | 7720
2026-07-01 | Acid plant | t H2SO4 | 744 | 713.8 | 18.8 | 8.3 | 3.1 | 18324 | 16920
2026-07-01 | Calciner | kg U3O8 | 744 | 698.8 | 27.5 | 16.6 | 1.1 | 63736 | 68750
2026-07-01 | Power plant | MWh | 744 | 684.1 | 34.8 | 18.4 | 6.7 | 6379 | 13920
2026-08-01 | Acid plant | t H2SO4 | 744 | 668.6 | 50 | 18.7 | 6.7 | 16926 | 45000
2026-08-01 | Calciner | kg U3O8 | 744 | 691.7 | 32.3 | 12.9 | 7.1 | 65050 | 80750
2026-08-01 | Power plant | MWh | 744 | 718.9 | 16.4 | 4.1 | 4.6 | 6964 | 6560
2026-09-01 | Acid plant | t H2SO4 | 720 | 673.8 | 21.8 | 18.3 | 6.1 | 15855 | 19620
2026-09-01 | Calciner | kg U3O8 | 720 | 663.4 | 36 | 17.1 | 3.5 | 60680 | 90000
2026-09-01 | Power plant | MWh | 720 | 658.1 | 46.3 | 10.1 | 5.5 | 6300 | 18520

## Maint_Costs
AHIM Maintenance cost against budget
One row per month, area and category (USD). Source: Finance / maintenance cost report. Frequency: Monthly. Key: Month + Area + Category.
Month | Area | Category | Budget (USD) | Actual (USD)
2025-10-01 | Acid plant | Labour | 26000 | 30342
2025-10-01 | Acid plant | Parts and materials | 19000 | 18717
2025-10-01 | Acid plant | Contractors | 11000 | 11026
2025-10-01 | Acid plant | Other | 2500 | 2893
2025-10-01 | Calciner | Labour | 9000 | 9398
2025-10-01 | Calciner | Parts and materials | 7000 | 7568
2025-10-01 | Calciner | Contractors | 4500 | 3939
2025-10-01 | Calciner | Other | 1000 | 996
2025-10-01 | Power plant | Labour | 8000 | 7457
2025-10-01 | Power plant | Parts and materials | 10500 | 9517
2025-10-01 | Power plant | Contractors | 4000 | 4165
2025-10-01 | Power plant | Other | 1000 | 976
2025-10-01 | Substation | Labour | 3000 | 3008
2025-10-01 | Substation | Parts and materials | 1500 | 1674
2025-10-01 | Substation | Contractors | 2000 | 1783
2025-10-01 | Substation | Other | 250 | 258
2025-10-01 | Mobile fleet | Labour | 4500 | 4569
2025-10-01 | Mobile fleet | Parts and materials | 8000 | 7281
2025-10-01 | Mobile fleet | Contractors | 1500 | 1465
2025-10-01 | Mobile fleet | Other | 500 | 510
2025-11-01 | Acid plant | Labour | 26000 | 26603
2025-11-01 | Acid plant | Parts and materials | 19000 | 16985
2025-11-01 | Acid plant | Contractors | 11000 | 10481
2025-11-01 | Acid plant | Other | 2500 | 2141
2025-11-01 | Calciner | Labour | 9000 | 9835
2025-11-01 | Calciner | Parts and materials | 7000 | 7930
2025-11-01 | Calciner | Contractors | 4500 | 4612
2025-11-01 | Calciner | Other | 1000 | 1084
2025-11-01 | Power plant | Labour | 8000 | 7323
2025-11-01 | Power plant | Parts and materials | 10500 | 12089
2025-11-01 | Power plant | Contractors | 4000 | 4037
2025-11-01 | Power plant | Other | 1000 | 1082
2025-11-01 | Substation | Labour | 3000 | 3200
2025-11-01 | Substation | Parts and materials | 1500 | 1421
2025-11-01 | Substation | Contractors | 2000 | 2131
2025-11-01 | Substation | Other | 250 | 223
2025-11-01 | Mobile fleet | Labour | 4500 | 5210
2025-11-01 | Mobile fleet | Parts and materials | 8000 | 9414
2025-11-01 | Mobile fleet | Contractors | 1500 | 1746
2025-11-01 | Mobile fleet | Other | 500 | 581
2025-12-01 | Acid plant | Labour | 26000 | 27749
2025-12-01 | Acid plant | Parts and materials | 19000 | 16775
2025-12-01 | Acid plant | Contractors | 11000 | 9780
2025-12-01 | Acid plant | Other | 2500 | 2192
2025-12-01 | Calciner | Labour | 9000 | 10246
2025-12-01 | Calciner | Parts and materials | 7000 | 7216
2025-12-01 | Calciner | Contractors | 4500 | 4485
2025-12-01 | Calciner | Other | 1000 | 942
2025-12-01 | Power plant | Labour | 8000 | 9193
2025-12-01 | Power plant | Parts and materials | 10500 | 10937
2025-12-01 | Power plant | Contractors | 4000 | 3569
2025-12-01 | Power plant | Other | 1000 | 966
2025-12-01 | Substation | Labour | 3000 | 3450
2025-12-01 | Substation | Parts and materials | 1500 | 1653
2025-12-01 | Substation | Contractors | 2000 | 2331
2025-12-01 | Substation | Other | 250 | 262
2025-12-01 | Mobile fleet | Labour | 4500 | 4865
2025-12-01 | Mobile fleet | Parts and materials | 8000 | 8759
2025-12-01 | Mobile fleet | Contractors | 1500 | 1342
2025-12-01 | Mobile fleet | Other | 500 | 467
2026-01-01 | Acid plant | Labour | 26000 | 30260
2026-01-01 | Acid plant | Parts and materials | 19000 | 17240
2026-01-01 | Acid plant | Contractors | 11000 | 12051
2026-01-01 | Acid plant | Other | 2500 | 2220
2026-01-01 | Calciner | Labour | 9000 | 7761
2026-01-01 | Calciner | Parts and materials | 7000 | 7570
2026-01-01 | Calciner | Contractors | 4500 | 4434
2026-01-01 | Calciner | Other | 1000 | 1066
2026-01-01 | Power plant | Labour | 8000 | 7682
2026-01-01 | Power plant | Parts and materials | 10500 | 11283
2026-01-01 | Power plant | Contractors | 4000 | 4565
2026-01-01 | Power plant | Other | 1000 | 1158
2026-01-01 | Substation | Labour | 3000 | 3287
2026-01-01 | Substation | Parts and materials | 1500 | 1304
2026-01-01 | Substation | Contractors | 2000 | 1960
2026-01-01 | Substation | Other | 250 | 255
2026-01-01 | Mobile fleet | Labour | 4500 | 4941
2026-01-01 | Mobile fleet | Parts and materials | 8000 | 6925
2026-01-01 | Mobile fleet | Contractors | 1500 | 1565
2026-01-01 | Mobile fleet | Other | 500 | 538
2026-02-01 | Acid plant | Labour | 26000 | 29432
2026-02-01 | Acid plant | Parts and materials | 30400 | 17400
2026-02-01 | Acid plant | Contractors | 17600 | 19952
2026-02-01 | Acid plant | Other | 4000 | 2484
2026-02-01 | Calciner | Labour | 9000 | 7825
2026-02-01 | Calciner | Parts and materials | 7000 | 8226
2026-02-01 | Calciner | Contractors | 4500 | 4955
2026-02-01 | Calciner | Other | 1000 | 975
2026-02-01 | Power plant | Labour | 8000 | 8689
2026-02-01 | Power plant | Parts and materials | 10500 | 10329
2026-02-01 | Power plant | Contractors | 4000 | 4645
2026-02-01 | Power plant | Other | 1000 | 899
2026-02-01 | Substation | Labour | 3000 | 2988
2026-02-01 | Substation | Parts and materials | 1500 | 1682
2026-02-01 | Substation | Contractors | 2000 | 2172
2026-02-01 | Substation | Other | 250 | 225
2026-02-01 | Mobile fleet | Labour | 4500 | 5291
2026-02-01 | Mobile fleet | Parts and materials | 8000 | 9227
2026-02-01 | Mobile fleet | Contractors | 1500 | 1689
2026-02-01 | Mobile fleet | Other | 500 | 448
2026-03-01 | Acid plant | Labour | 26000 | 30408
2026-03-01 | Acid plant | Parts and materials | 19000 | 21293
2026-03-01 | Acid plant | Contractors | 11000 | 11495
2026-03-01 | Acid plant | Other | 2500 | 2236
2026-03-01 | Calciner | Labour | 9000 | 10041
2026-03-01 | Calciner | Parts and materials | 7000 | 7498
2026-03-01 | Calciner | Contractors | 4500 | 4874
2026-03-01 | Calciner | Other | 1000 | 907
2026-03-01 | Power plant | Labour | 8000 | 7610
2026-03-01 | Power plant | Parts and materials | 10500 | 9532
2026-03-01 | Power plant | Contractors | 4000 | 3510
2026-03-01 | Power plant | Other | 1000 | 1061
2026-03-01 | Substation | Labour | 3000 | 2895
2026-03-01 | Substation | Parts and materials | 1500 | 1765
2026-03-01 | Substation | Contractors | 2000 | 2261
2026-03-01 | Substation | Other | 250 | 258
2026-03-01 | Mobile fleet | Labour | 4500 | 3903
2026-03-01 | Mobile fleet | Parts and materials | 8000 | 8032
2026-03-01 | Mobile fleet | Contractors | 1500 | 1515
2026-03-01 | Mobile fleet | Other | 500 | 437
2026-04-01 | Acid plant | Labour | 26000 | 30006
2026-04-01 | Acid plant | Parts and materials | 19000 | 21308
2026-04-01 | Acid plant | Contractors | 11000 | 11026
2026-04-01 | Acid plant | Other | 2500 | 2766
2026-04-01 | Calciner | Labour | 9000 | 9436
2026-04-01 | Calciner | Parts and materials | 7000 | 7340
2026-04-01 | Calciner | Contractors | 4500 | 4077
2026-04-01 | Calciner | Other | 1000 | 1126
2026-04-01 | Power plant | Labour | 8000 | 7766
2026-04-01 | Power plant | Parts and materials | 10500 | 9141
2026-04-01 | Power plant | Contractors | 4000 | 4251
2026-04-01 | Power plant | Other | 1000 | 957
2026-04-01 | Substation | Labour | 3000 | 3037
2026-04-01 | Substation | Parts and materials | 1500 | 1515
2026-04-01 | Substation | Contractors | 2000 | 1831
2026-04-01 | Substation | Other | 250 | 215
2026-04-01 | Mobile fleet | Labour | 4500 | 4716
2026-04-01 | Mobile fleet | Parts and materials | 8000 | 7354
2026-04-01 | Mobile fleet | Contractors | 1500 | 1721
2026-04-01 | Mobile fleet | Other | 500 | 530
2026-05-01 | Acid plant | Labour | 26000 | 28179
2026-05-01 | Acid plant | Parts and materials | 19000 | 19624
2026-05-01 | Acid plant | Contractors | 11000 | 12680
2026-05-01 | Acid plant | Other | 2500 | 2175
2026-05-01 | Calciner | Labour | 9000 | 9342
2026-05-01 | Calciner | Parts and materials | 7000 | 6681
2026-05-01 | Calciner | Contractors | 4500 | 3921
2026-05-01 | Calciner | Other | 1000 | 1139
2026-05-01 | Power plant | Labour | 8000 | 8320
2026-05-01 | Power plant | Parts and materials | 10500 | 11504
2026-05-01 | Power plant | Contractors | 4000 | 4382
2026-05-01 | Power plant | Other | 1000 | 880
2026-05-01 | Substation | Labour | 3000 | 3055
2026-05-01 | Substation | Parts and materials | 1500 | 1452
2026-05-01 | Substation | Contractors | 2000 | 1730
2026-05-01 | Substation | Other | 250 | 264
2026-05-01 | Mobile fleet | Labour | 4500 | 4840
2026-05-01 | Mobile fleet | Parts and materials | 8000 | 8322
2026-05-01 | Mobile fleet | Contractors | 1500 | 1424
2026-05-01 | Mobile fleet | Other | 500 | 479
2026-06-01 | Acid plant | Labour | 26000 | 26591
2026-06-01 | Acid plant | Parts and materials | 19000 | 18762
2026-06-01 | Acid plant | Contractors | 11000 | 11848
2026-06-01 | Acid plant | Other | 2500 | 2405
2026-06-01 | Calciner | Labour | 9000 | 10189
2026-06-01 | Calciner | Parts and materials | 7000 | 7362
2026-06-01 | Calciner | Contractors | 4500 | 4861
2026-06-01 | Calciner | Other | 1000 | 968
2026-06-01 | Power plant | Labour | 8000 | 7877
2026-06-01 | Power plant | Parts and materials | 10500 | 12022
2026-06-01 | Power plant | Contractors | 4000 | 4657
2026-06-01 | Power plant | Other | 1000 | 1106
2026-06-01 | Substation | Labour | 3000 | 3345
2026-06-01 | Substation | Parts and materials | 1500 | 1768
2026-06-01 | Substation | Contractors | 2000 | 1788
2026-06-01 | Substation | Other | 250 | 238
2026-06-01 | Mobile fleet | Labour | 4500 | 4386
2026-06-01 | Mobile fleet | Parts and materials | 8000 | 7715
2026-06-01 | Mobile fleet | Contractors | 1500 | 1398
2026-06-01 | Mobile fleet | Other | 500 | 441
2026-07-01 | Acid plant | Labour | 26000 | 29227
2026-07-01 | Acid plant | Parts and materials | 19000 | 19503
2026-07-01 | Acid plant | Contractors | 11000 | 11590
2026-07-01 | Acid plant | Other | 2500 | 2806
2026-07-01 | Calciner | Labour | 9000 | 7972
2026-07-01 | Calciner | Parts and materials | 7000 | 6962
2026-07-01 | Calciner | Contractors | 4500 | 4513
2026-07-01 | Calciner | Other | 1000 | 976
2026-07-01 | Power plant | Labour | 8000 | 7625
2026-07-01 | Power plant | Parts and materials | 10500 | 12267
2026-07-01 | Power plant | Contractors | 4000 | 3478
2026-07-01 | Power plant | Other | 1000 | 995
2026-07-01 | Substation | Labour | 3000 | 3364
2026-07-01 | Substation | Parts and materials | 1500 | 1639
2026-07-01 | Substation | Contractors | 2000 | 1715
2026-07-01 | Substation | Other | 250 | 220
2026-07-01 | Mobile fleet | Labour | 4500 | 4078
2026-07-01 | Mobile fleet | Parts and materials | 8000 | 7998
2026-07-01 | Mobile fleet | Contractors | 1500 | 1487
2026-07-01 | Mobile fleet | Other | 500 | 565
2026-08-01 | Acid plant | Labour | 26000 | 30476
2026-08-01 | Acid plant | Parts and materials | 19000 | 19675
2026-08-01 | Acid plant | Contractors | 11000 | 10110
2026-08-01 | Acid plant | Other | 2500 | 2740
2026-08-01 | Calciner | Labour | 9000 | 9778
2026-08-01 | Calciner | Parts and materials | 7000 | 8034
2026-08-01 | Calciner | Contractors | 4500 | 4356
2026-08-01 | Calciner | Other | 1000 | 1048
2026-08-01 | Power plant | Labour | 8000 | 8939
2026-08-01 | Power plant | Parts and materials | 10500 | 10596
2026-08-01 | Power plant | Contractors | 4000 | 4077
2026-08-01 | Power plant | Other | 1000 | 1077
2026-08-01 | Substation | Labour | 3000 | 2772
2026-08-01 | Substation | Parts and materials | 1500 | 1632
2026-08-01 | Substation | Contractors | 2000 | 2086
2026-08-01 | Substation | Other | 250 | 281
2026-08-01 | Mobile fleet | Labour | 4500 | 4020
2026-08-01 | Mobile fleet | Parts and materials | 8000 | 9031
2026-08-01 | Mobile fleet | Contractors | 1500 | 1656
2026-08-01 | Mobile fleet | Other | 500 | 546
2026-09-01 | Acid plant | Labour | 26000 | 29455
2026-09-01 | Acid plant | Parts and materials | 19000 | 19256
2026-09-01 | Acid plant | Contractors | 11000 | 10979
2026-09-01 | Acid plant | Other | 2500 | 2347
2026-09-01 | Calciner | Labour | 9000 | 9579
2026-09-01 | Calciner | Parts and materials | 7000 | 5960
2026-09-01 | Calciner | Contractors | 4500 | 4519
2026-09-01 | Calciner | Other | 1000 | 1180
2026-09-01 | Power plant | Labour | 8000 | 7666
2026-09-01 | Power plant | Parts and materials | 10500 | 9536
2026-09-01 | Power plant | Contractors | 4000 | 3947
2026-09-01 | Power plant | Other | 1000 | 1087
2026-09-01 | Substation | Labour | 3000 | 3383
2026-09-01 | Substation | Parts and materials | 1500 | 1337
2026-09-01 | Substation | Contractors | 2000 | 2040
2026-09-01 | Substation | Other | 250 | 281
2026-09-01 | Mobile fleet | Labour | 4500 | 5107
2026-09-01 | Mobile fleet | Parts and materials | 8000 | 8617
2026-09-01 | Mobile fleet | Contractors | 1500 | 1420
2026-09-01 | Mobile fleet | Other | 500 | 439

## Labour
AHIM Maintenance labour hours
One row per month and trade: hours available, worked, on planned work, on emergency work, overtime. Source: Maintenance supervisors / timesheets. Frequency: Monthly. Key: Month + Trade.
Month | Trade | Available hours | Worked hours | Planned-work hours | Emergency hours | Overtime hours
2025-10-01 | Mechanical | 1408 | 1306 | 865 | 257 | 82
2025-10-01 | Electrical | 704 | 638 | 453 | 122 | 63
2025-10-01 | Instrumentation | 352 | 328 | 231 | 62 | 27
2025-10-01 | Boilermaker | 528 | 490 | 348 | 84 | 30
2025-10-01 | Fleet | 528 | 476 | 334 | 79 | 51
2025-11-01 | Mechanical | 1408 | 1308 | 913 | 244 | 105
2025-11-01 | Electrical | 704 | 643 | 444 | 109 | 55
2025-11-01 | Instrumentation | 352 | 332 | 231 | 53 | 21
2025-11-01 | Boilermaker | 528 | 487 | 349 | 89 | 35
2025-11-01 | Fleet | 528 | 486 | 338 | 83 | 31
2025-12-01 | Mechanical | 1408 | 1289 | 915 | 225 | 166
2025-12-01 | Electrical | 704 | 644 | 445 | 109 | 35
2025-12-01 | Instrumentation | 352 | 339 | 248 | 60 | 19
2025-12-01 | Boilermaker | 528 | 510 | 354 | 90 | 36
2025-12-01 | Fleet | 528 | 488 | 341 | 72 | 31
2026-01-01 | Mechanical | 1408 | 1340 | 967 | 185 | 135
2026-01-01 | Electrical | 704 | 674 | 479 | 104 | 56
2026-01-01 | Instrumentation | 352 | 323 | 233 | 45 | 31
2026-01-01 | Boilermaker | 528 | 511 | 359 | 85 | 36
2026-01-01 | Fleet | 528 | 512 | 371 | 75 | 63
2026-02-01 | Mechanical | 1408 | 1319 | 941 | 197 | 123
2026-02-01 | Electrical | 704 | 669 | 514 | 89 | 39
2026-02-01 | Instrumentation | 352 | 328 | 244 | 54 | 24
2026-02-01 | Boilermaker | 528 | 493 | 360 | 78 | 62
2026-02-01 | Fleet | 528 | 491 | 377 | 61 | 38
2026-03-01 | Mechanical | 1408 | 1270 | 940 | 192 | 183
2026-03-01 | Electrical | 704 | 663 | 504 | 88 | 58
2026-03-01 | Instrumentation | 352 | 330 | 252 | 40 | 43
2026-03-01 | Boilermaker | 528 | 500 | 389 | 61 | 47
2026-03-01 | Fleet | 528 | 502 | 389 | 64 | 35
2026-04-01 | Mechanical | 1408 | 1311 | 1006 | 162 | 86
2026-04-01 | Electrical | 704 | 647 | 509 | 94 | 52
2026-04-01 | Instrumentation | 352 | 322 | 253 | 46 | 26
2026-04-01 | Boilermaker | 528 | 496 | 396 | 70 | 50
2026-04-01 | Fleet | 528 | 498 | 385 | 63 | 42
2026-05-01 | Mechanical | 1408 | 1365 | 1092 | 159 | 94
2026-05-01 | Electrical | 704 | 638 | 496 | 75 | 80
2026-05-01 | Instrumentation | 352 | 340 | 259 | 41 | 41
2026-05-01 | Boilermaker | 528 | 500 | 399 | 51 | 48
2026-05-01 | Fleet | 528 | 499 | 380 | 51 | 30
2026-06-01 | Mechanical | 1408 | 1274 | 1015 | 147 | 163
2026-06-01 | Electrical | 704 | 679 | 548 | 85 | 67
2026-06-01 | Instrumentation | 352 | 330 | 255 | 34 | 20
2026-06-01 | Boilermaker | 528 | 503 | 391 | 46 | 33
2026-06-01 | Fleet | 528 | 483 | 382 | 59 | 48
2026-07-01 | Mechanical | 1408 | 1313 | 1047 | 125 | 81
2026-07-01 | Electrical | 704 | 674 | 545 | 71 | 55
2026-07-01 | Instrumentation | 352 | 325 | 259 | 28 | 45
2026-07-01 | Boilermaker | 528 | 495 | 410 | 50 | 37
2026-07-01 | Fleet | 528 | 482 | 400 | 54 | 35
2026-08-01 | Mechanical | 1408 | 1321 | 1070 | 122 | 73
2026-08-01 | Electrical | 704 | 673 | 540 | 67 | 79
2026-08-01 | Instrumentation | 352 | 331 | 270 | 24 | 23
2026-08-01 | Boilermaker | 528 | 500 | 427 | 44 | 34
2026-08-01 | Fleet | 528 | 508 | 406 | 48 | 57
2026-09-01 | Mechanical | 1408 | 1284 | 1091 | 91 | 97
2026-09-01 | Electrical | 704 | 664 | 545 | 57 | 51
2026-09-01 | Instrumentation | 352 | 341 | 286 | 23 | 42
2026-09-01 | Boilermaker | 528 | 500 | 415 | 33 | 32
2026-09-01 | Fleet | 528 | 505 | 421 | 49 | 61

## RCA
AHIM Root cause analysis tracker
One row per RCA. Status moves Open > Analysis > Actions in progress > Effectiveness check > Closed. Source: Reliability engineer. Frequency: When raised, updated weekly. Key: RCA no..
RCA no. | Pronto asset no. | Trigger | Raised | Lead | Problem | Root cause | Status | Due | Closed | Effective (Y/N) | Annual saving (USD)
RCA-2025-07 | 100404 | Breakdown | 2025-12-08 | Reliability Engineer | Fuel injector failure, unit offline 10 h | Contaminated fuel: day-tank filter bypassed | Closed | 2026-01-31 | 2026-01-20 | Y | 18000
RCA-2026-02 | 100102 | Breakdown | 2026-02-18 | Integrity Engineer | Economiser tube leak, 36 h plant stop | Oxygen pitting: deaerator control out of range | Closed | 2026-04-30 | 2026-04-22 | Y | 95000
RCA-2026-03 | 100401 | Breakdown | 2026-03-14 | Reliability Engineer | Turbo oil feed line leak, unit stopped | Line chafing on bracket: clamp missing after overhaul | Actions in progress | 2026-06-30 |  |  | 0
RCA-2026-04 | 100105 | Bad actor | 2026-04-25 | RCM Specialist | Repeat DE bearing failures on drying tower pump | Soft foot and pipe strain after each repair | Effectiveness check | 2026-07-31 |  |  | 40000
RCA-2026-07 | 100114 | Breakdown | 2026-07-08 | Integrity Engineer | Pinhole leak at elbow E-04 | Velocity above limit for carbon steel in acid service | Analysis | 2026-09-15 |  |  | 0
RCA-2026-09 | 100112 | Danger finding | 2026-09-12 | RCM Specialist | Cooling tower gearbox gear-mesh deterioration |  | Open | 2026-10-31 |  |  | 0

## Actions
AHIM Action tracker
All actions from management decisions, RCAs, CM meetings, risk treatment and audits, with evidence of closure. Source: Action owners, reviewed in the CM meeting. Frequency: Weekly. Key: Action no..
Action no. | Source | Reference | Action | Owner | Raised | Due | Status | Closed | Evidence
ACT-001 | Management decision | DEC-01 | Approve and plan the October 36-hour stop | Engineering Manager | 2026-09-25 | 2026-10-05 | In progress
ACT-002 | Management decision | DEC-02 | Book statutory inspector for the waste heat boiler | Engineering Manager | 2026-09-02 | 2026-09-30 | Open
ACT-003 | RCA | RCA-2026-04 | Install pipe supports on P-101 suction and discharge | Mechanical Supervisor | 2026-05-10 | 2026-06-30 | Done | 2026-06-20 | WO 243700 closed, photos
ACT-004 | RCA | RCA-2026-04 | Soft-foot check added to pump alignment procedure | RCM Specialist | 2026-05-10 | 2026-06-15 | Done | 2026-06-12 | Procedure rev 3
ACT-005 | RCA | RCA-2026-03 | Add clamp check to generator overhaul checklist | Power Plant Supervisor | 2026-04-02 | 2026-05-15 | Open
ACT-006 | RCA | RCA-2026-07 | Velocity survey of acid lines; resize where above limit | Integrity Engineer | 2026-08-01 | 2026-10-15 | In progress
ACT-007 | CM and planning meeting | CM-W36 | Raise WOs for all P1 findings without a WO | Planner | 2026-09-04 | 2026-09-08 | Done | 2026-09-08 | WO list in meeting minutes
ACT-008 | CM and planning meeting | CM-W38 | Re-plan vibration route around production schedule | RCM Specialist | 2026-09-18 | 2026-09-30 | In progress
ACT-009 | CM and planning meeting | CM-W39 | Clear backlog items older than 90 days | Maintenance Superintendent | 2026-09-25 | 2026-10-31 | Open
ACT-010 | Risk treatment | RISK-SS-MCC-01 | Thermal camera check of MCC after re-termination | Electrical Supervisor | 2026-09-25 | 2026-10-02 | Open
ACT-011 | Risk treatment | RISK-AP-PL-01 | Isolate acid line E-07 section until spool replaced | Area Superintendent | 2026-09-19 | 2026-09-22 | Done | 2026-09-21 | Isolation certificate
ACT-012 | Audit | AUD-2026-1 | Document criticality method and approve | RCM Specialist | 2026-03-01 | 2026-06-30 | In progress
ACT-013 | Management review | MR-Q3 | Approve KPI targets and risk matrix | Engineering Manager | 2026-07-15 | 2026-08-31 | Done | 2026-08-28 | Signed framework
ACT-014 | Management review | MR-Q3 | Fund online vibration monitoring for main blower | General Manager | 2026-07-15 | 2026-12-15 | Open

## KPI_Tree
AHIM KPI tree: objectives, KPIs, owners and targets
Line of sight from asset management objectives to KPIs. KPI id links to the calculation in the dashboard: do not change ids. Source: Engineering Manager (approves). Frequency: Annual review. Key: KPI id.
KPI id | Objective | KPI | Tier | Owner | Target | Direction | Frequency
extreme_risks | 1. Safe and compliant operation | Extreme risks | Strategic | General Manager | 0 | Lower is better | Monthly
statutory | 1. Safe and compliant operation | Statutory inspections in date (%) | Strategic | Engineering Manager | 100 | Higher is better | Monthly
p1_overdue | 1. Safe and compliant operation | P1 findings overdue | Tactical | Maintenance Superintendent | 0 | Lower is better | Weekly
availability | 2. Reliable production | Availability of critical circuits (%) | Strategic | Engineering Manager | 95 | Higher is better | Monthly
downtime_cost | 2. Reliable production | Maintenance downtime cost, month (USD) | Strategic | Engineering Manager | 100000 | Lower is better | Monthly
ahi | 2. Reliable production | Asset Health Index | Strategic | RCM Specialist | 85 | Higher is better | Monthly
bad_actor_rca | 2. Reliable production | Bad actors with an RCA (%) | Tactical | Reliability Engineer | 100 | Higher is better | Monthly
pm_compliance | 3. Effective maintenance execution | PM compliance (%) | Tactical | Planner | 90 | Higher is better | Weekly
schedule_compliance | 3. Effective maintenance execution | Schedule compliance (%) | Tactical | Planner | 85 | Higher is better | Weekly
planned_work | 3. Effective maintenance execution | Planned work, % of hours | Tactical | Maintenance Superintendent | 85 | Higher is better | Monthly
reactive_work | 3. Effective maintenance execution | Emergency work, % of hours | Tactical | Maintenance Superintendent | 10 | Lower is better | Monthly
backlog_weeks | 3. Effective maintenance execution | Backlog (crew-weeks) | Tactical | Planner | 4 | Lower is better | Weekly
findings_wo | 3. Effective maintenance execution | Open findings with a work order (%) | Operational | Planner | 100 | Higher is better | Weekly
cost_budget | 4. Cost-effective maintenance | Maintenance cost vs budget, YTD (%) | Strategic | Engineering Manager | 100 | Lower is better | Monthly
cost_rav | 4. Cost-effective maintenance | Maintenance cost, % of replacement asset value | Strategic | Engineering Manager | 3.5 | Lower is better | Annual
cm_roi | 4. Cost-effective maintenance | CM return on investment (x : 1) | Strategic | RCM Specialist | 4 | Higher is better | Monthly
data_confidence | 5. Known and controlled asset condition | Data confidence (%) | Tactical | RCM Specialist | 85 | Higher is better | Monthly
strategy_compliance | 5. Known and controlled asset condition | Strategy compliance, critical assets (%) | Tactical | RCM Specialist | 90 | Higher is better | Monthly
actions_overdue | 6. Governance and improvement | Overdue actions | Tactical | Engineering Manager | 0 | Lower is better | Weekly

## Routes
AHIM Inspection routes
One row per route: interval and last completion drive the Field page. Assets = Pronto asset numbers separated by commas. Source: RCM Specialist. Frequency: Each route completion. Key: Route ID.
Route ID | Route | Area | Technique | Technician | Interval (days) | Last completed | Assets
R-AP-VIB | Acid plant vibration route | Acid plant | Vibration | CM Technician 1 | 30 | 2026-09-22 | 100103,100105,100106,100107,100108,100109,100110,100111,100112
R-AP-VIS | Acid plant sensitive inspection | Acid plant | Visual | CM Technician 2 | 7 | 2026-09-21 | 100101,100102,100104,100113,100114,100115,100105,100106
R-AP-IR | Acid plant IR survey | Acid plant | Infrared | RCM Specialist | 30 | 2026-09-08 | 100101,100104,100102
R-SS-IR | Substation IR and ultrasound | Substation | Infrared | RCM Specialist | 30 | 2026-08-24 | 100301,100302
R-CK-IR | Calciner shell scan | Calciner | Infrared | RCM Specialist | 30 | 2026-09-26 | 100201
R-PP-DG | Power plant daily DG log | Power plant | DG checks | DG Operator | 1 | 2026-09-28 | 100401,100402,100403,100404
R-OIL | Oil sampling route | Acid plant | Lubrication / oil | CM Technician 1 | 30 | 2026-09-05 | 100105,100108,100112,100201
R-FL-PS | Fleet prestart audit | Mobile fleet | Prestart | Fleet Supervisor | 7 | 2026-09-18 | 100501,100502,100601,100602,100603

## Risk_Consequence
Risk matrix: consequence levels (uranium process and sulphuric acid plant)
Worst credible consequence across seven categories; the highest category sets the level. Dose criteria per ICRP 103 / IAEA GSR Part 3. Financial bands to be calibrated with site finance.
Level | Name | Safety | Health and radiation | Environment | Production | Financial | Regulatory and legal | Community and reputation
1 | Insignificant | First aid case | No measurable dose or contamination above normal operating levels; chemical exposure below OEL | Release contained within bund or process area; cleaned up within the shift; no environmental impact | Under 1 h of circuit downtime, or a standby unit lost with no throughput loss | Under USD 10k (repair and lost production) | Internal non-conformance only; no external reporting | No external interest
2 | Minor | Medical treatment or restricted work case | Event dose under 1 mSv; skin or PPE contamination removed on site; uranium bioassay below investigation level; brief exposure to acid mist, SO2 or H2O2 with no treatment | Small release outside bund, on site only, cleaned up within 24 h; no breach of discharge or emission limits | 1 to 8 h circuit outage, or under 5% of daily U3O8 production lost | USD 10k to 100k | Minor non-compliance with a licence or permit condition, closed out in routine reporting | Local concern handled through normal community engagement
3 | Moderate | Lost-time injury, fully reversible | Event dose 1 to 5 mSv or above the site investigation level; internal contamination (bioassay above investigation level); exposure above OEL to acid, SO2/SO3 or H2O2 needing medical assessment | Reportable on-site release of acid, uranium-bearing solution or slurry; short exceedance of an emission or discharge limit; remediation within 1 month | 8 to 24 h circuit stop, or 5 to 25% of daily production lost; acid plant trip limiting leach acid supply | USD 100k to 500k | Notifiable incident to the radiation or environmental regulator; inspection or improvement notice likely | Formal community complaint or local media coverage
4 | Major | Permanent disability, or several lost-time injuries in one event | Occupational dose limit exceeded (ICRP 103: 20 mSv/y averaged over 5 years, or 50 mSv in one year) or public dose above 1 mSv/y; uranium intake requiring clinical follow-up; occupational illness | Off-site release of acid, uranium-bearing solution, slurry or tailings water to surface or groundwater; off-site SO2 impact; remediation over months | 1 to 7 days plant stop, or over 25% of weekly production lost | USD 0.5M to 2.5M | Breach of licence or permit conditions; regulatory directive or fine; loss of control of uranium concentrate requiring nuclear security or safeguards reporting | National media coverage, community protest, or offtaker or investor concern
5 | Catastrophic | One or more fatalities | Severe overexposure with deterministic effects, several workers over the dose limit, or public exposure needing protective action; fatality or chronic disease from exposure | Major off-site release (tailings storage, leach circuit or acid storage failure) with long-term contamination of water resources or ecosystems; remediation over years | Over 7 days plant stop, or a month of production target lost | Over USD 2.5M | Licence suspension or revocation, prosecution, or shutdown ordered by a regulator; theft or diversion of uranium concentrate | International coverage; sustained loss of social licence to operate

## Risk_Likelihood
Risk matrix: likelihood levels
Frequency guide for risk assessments; AHIM sets likelihood from condition (an open finding can override it: Records, Likelihood override).
Level | Name | Description | Frequency guide | AHIM mapping
1 | Rare | Not expected in the life of the asset | Less than once in 20 years | Condition OK and inspected within its required interval
2 | Unlikely | Could occur at some time | Once in 5 to 20 years | Condition Unknown: not inspected within its required interval
3 | Possible | Deterioration confirmed; failure could occur | Once in 1 to 5 years | Open Alert finding, or latest reading in the alert band
4 | Likely | Failure expected within weeks to months | About once a year or more | Open Danger finding, latest reading in the danger band, or remaining life 1 year or less
5 | Almost certain | Failure in progress or imminent | Several times a year, or happening now | Active loss of containment, through-wall defect, trip or failure in progress

## Risk_Rating
Risk matrix: rating, response and acceptance authority
Risk score = consequence x likelihood (1 to 25). A risk may only be accepted, unmitigated, by the authority shown or above.
Rating | Minimum score | Required response | Authority to accept the risk
Extreme | 20 | Act within 7 days; inform senior management; stop or restrict operation unless controls make it safe | General Manager
High | 12 | Act within 30 days; interim controls in place and verified; Engineering Manager informed | Engineering Manager
Medium | 5 | Plan within 90 days through normal planning and scheduling | Area Superintendent
Low | 1 | Manage by routine maintenance and monitoring | Supervisor

## Consequence_Floors
Consequence floors by service
Minimum consequence for equipment that holds or moves the fluid (loss of containment). Every asset handling dry uranium product takes the product floor. Read-only reference: change in scripts/ahim_reference.py.
Service | Minimum consequence | Reason | Applies to
Uranium product (yellowcake) | 4 | uranium concentrate: inhalation dose, emissions and nuclear security | All assets in the area
Sulphuric acid | 4 | sulphuric acid: severe burns and off-site release | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Hydrogen peroxide | 4 | hydrogen peroxide: oxidiser, decomposition and overpressure | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Uranium precipitate | 3 | uranium-bearing precipitate: contamination and dose | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Eluate / uranium solution | 3 | uranium-bearing solution: contamination and environmental release | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Slurry (acid leach) | 3 | acidic uranium-bearing slurry: environmental release | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Caustic soda | 3 | caustic: severe burns | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Gypsum slurry | 2 | gypsum slurry spill | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Slurry | 2 | slurry spill | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Reagent | 2 | reagent spill | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers
Water | 1 | water | Pumps, tanks, vessels, piping, heat exchangers, sumps, thickeners, acid towers and coolers

## Failure_Codes
ISO 14224 failure codes
Failure modes (what the failure looks like) and mechanisms (how it happens), ISO 14224:2016 Annex B, plus the mapping of site failure-mode text.
Type | Code | Description | Note
ISO 14224 failure mode | AIR | Abnormal instrument reading
ISO 14224 failure mode | BRD | Breakdown
ISO 14224 failure mode | ELP | External leakage - process medium
ISO 14224 failure mode | ELU | External leakage - utility medium
ISO 14224 failure mode | ERO | Erratic output
ISO 14224 failure mode | FTS | Fail to start on demand
ISO 14224 failure mode | HIO | High output
ISO 14224 failure mode | INL | Internal leakage
ISO 14224 failure mode | LOO | Low output
ISO 14224 failure mode | NOI | Noise
ISO 14224 failure mode | OHE | Overheating
ISO 14224 failure mode | PDE | Parameter deviation
ISO 14224 failure mode | PLU | Plugged / choked
ISO 14224 failure mode | SER | Minor in-service problems
ISO 14224 failure mode | STD | Structural deficiency
ISO 14224 failure mode | UST | Spurious stop
ISO 14224 failure mode | VIB | Vibration
ISO 14224 failure mode | OTH | Other
ISO 14224 failure mode | UNK | Unknown
ISO 14224 failure mechanism | 1.0 | Mechanical failure - general
ISO 14224 failure mechanism | 1.1 | Leakage
ISO 14224 failure mechanism | 1.2 | Vibration
ISO 14224 failure mechanism | 1.3 | Clearance / alignment failure
ISO 14224 failure mechanism | 1.4 | Deformation
ISO 14224 failure mechanism | 1.5 | Looseness
ISO 14224 failure mechanism | 1.6 | Sticking
ISO 14224 failure mechanism | 2.0 | Material failure - general
ISO 14224 failure mechanism | 2.1 | Cavitation
ISO 14224 failure mechanism | 2.2 | Corrosion
ISO 14224 failure mechanism | 2.3 | Erosion
ISO 14224 failure mechanism | 2.4 | Wear
ISO 14224 failure mechanism | 2.5 | Breakage
ISO 14224 failure mechanism | 2.6 | Fatigue
ISO 14224 failure mechanism | 2.7 | Overheating
ISO 14224 failure mechanism | 2.8 | Burst
ISO 14224 failure mechanism | 3.0 | Instrument failure - general
ISO 14224 failure mechanism | 4.0 | Electrical failure - general
ISO 14224 failure mechanism | 4.1 | Short circuiting
ISO 14224 failure mechanism | 4.2 | Open circuit
ISO 14224 failure mechanism | 4.3 | No power / voltage
ISO 14224 failure mechanism | 4.4 | Faulty power / voltage
ISO 14224 failure mechanism | 4.5 | Earth / isolation fault
ISO 14224 failure mechanism | 5.0 | External influence - general
ISO 14224 failure mechanism | 5.1 | Blockage / plugged
ISO 14224 failure mechanism | 5.2 | Contamination
ISO 14224 failure mechanism | 5.3 | Miscellaneous external influences
ISO 14224 failure mechanism | 6.0 | Miscellaneous
ISO 14224 failure mechanism | 6.4 | Unknown
Site failure mode mapping | Gear wear or breakage | NOI / 2.4 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Motor failure | BRD / 4.0 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Bearing failure | VIB / 2.4 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Shaft misalignment or bending | VIB / 1.3 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | VFD fault or failure | UST / 4.4 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Looseness on structures | VIB / 1.5 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Excessive vibration | VIB / 1.2 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Belt slippage or wear | LOO / 2.4 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Conveyor belt misalignment or tearing | STD / 1.3 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Hydraulic system leaks or pressure loss | ELU / 1.1 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Pump cavitation or seal failure | ELP / 2.1 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Valve leakage or malfunction | INL / 1.1 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Grounding issues | SER / 4.5 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Overloading of equipment | OHE / 2.7 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Agitator shaft failure | BRD / 2.5 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Fan imbalance or blade damage | VIB / 1.2 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Screen blinding or damage | PLU / 5.1 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Filter media blinding or damage | PLU / 5.1 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Lubrication system failure | OHE / 2.7 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Cracks in welds or joints | STD / 2.6 | CM workbook Failure Mode -> ISO 14224
Site failure mode mapping | Other | OTH / 6.0 | CM workbook Failure Mode -> ISO 14224

## Damage_Mechanisms
Damage mechanisms (static equipment)
API 571 damage mechanisms and site mechanisms relevant to the uranium process plant and the sulphuric acid plant.
Mechanism | Source | Where it applies
Sulfuric acid corrosion | API 571 | Acid plant towers, coolers, acid tanks and piping; leach and reagent tanks. Velocity, temperature and concentration sensitive.
Erosion / erosion-corrosion | API 571 | Slurry tanks, launders, slurry piping and pump casings; leach and RIP circuits.
Atmospheric corrosion | API 571 | External surfaces; accelerated by acid vapour and water retention on roofs.
Corrosion under insulation (CUI) | API 571 | Insulated tanks and piping, especially cycling temperatures.
Flue-gas dew-point corrosion | API 571 | Acid plant gas ducts, economisers and converter outlets below acid dew point.
Mechanical / vibration fatigue | API 571 | Agitator bridges, screen side plates, small-bore connections.
Refractory degradation | API 571 / API RP 936 | Sulphur furnace, converter, kiln and calciner linings: detected by IR hot spots.
Boiler water / condensate corrosion | API 571 | Waste heat boiler and economiser water side.
Localized (pitting) corrosion | Site | Coating defects, crevices, stagnant zones.
Coating breakdown | Site / ISO 12944 | External coating failure leading to atmospheric or acid-vapour corrosion.
Lining failure | Site | Rubber or FRP lining holidays in acid and leach service.
Gasket / bolting degradation | Site / ASME PCC-1 | Flanges and manways: loss of preload, chemical attack of gaskets, missing bolts.
Concrete acid attack | Site | Foundations, plinths and bunds exposed to acid spillage.
Foundation settlement | Site / API 653 Annex B | Tank foundations: tilt, settlement, loss of anchorage.
Weld cracking / weld defects | Site | Repaired welds, lack of fusion, fatigue cracks at shell-to-bottom.
Wall thinning (general) | Site | Measured loss of thickness where the mechanism is not yet confirmed.

## Strategy_Library
Equipment strategy library
Failure mode -> technique -> task -> interval by criticality class (A/B/C, days; blank = not required). Starting intervals: refine with P-F interval, history and OEM (ISO 17359). Tracked = N: done by operators, not measured in AHIM.
Strategy class | Failure mode (ISO 14224) | Mechanism / cause | Technique | Task | Interval A (days) | Interval B (days) | Interval C (days) | Alert / Danger criterion | Reference | Tracked in AHIM
Centrifugal slurry pump | VIB | Bearing wear, misalignment, looseness, unbalance | Vibration | Overall velocity and bearing envelope (gE) route, all bearings, 3 axes | 30 | 60 | 90 | Velocity Alert 4.5 / Danger 7.1 mm/s RMS; gE 2x / 4x baseline | ISO 20816-3, ISO 13373-1 | Y
Centrifugal slurry pump | OHE | Bearing lubrication (over / under greasing) | Ultrasonics (airborne) | Ultrasound bearing condition and guided greasing | 30 | 60 | 90 | +8 dB over baseline Alert, +16 dB Danger | ISO 29821 | Y
Centrifugal slurry pump | OHE | Bearing, coupling and motor overheating | Infrared | Thermography of motor, coupling and bearing housings | 90 | 180 | 365 | Bearing dT > 20 C vs similar Alert, > 40 C Danger | ISO 18434-1 | Y
Centrifugal slurry pump | LOO | Wet-end wear (impeller, liner, throatbush) | Visual | CM sensitive inspection: duty point, gland, noise, casing wear | 30 | 60 | 90 | Performance < 90% of baseline Alert | OEM, ISO 17359 | Y
Centrifugal slurry pump | ELP | Gland / mechanical seal leakage | Visual | Operator round: gland leakage and flush water | 1 | 1 | 7 | Any slurry spray or acid leak = Danger | Site | N
Centrifugal slurry pump | STD | Casing / base erosion-corrosion | Ultrasonic thickness | UT of casing and suction / discharge spools at CMLs | 365 | 730 |  | Below minimum wall = Danger | API 570 practice | Y
Centrifugal process pump | VIB | Bearing wear, misalignment, cavitation | Vibration | Overall velocity and envelope route | 30 | 60 | 90 | Alert 4.5 / Danger 7.1 mm/s RMS | ISO 20816-3 | Y
Centrifugal process pump | OHE | Lubricant degradation, water ingress | Lubrication / oil | Oil analysis of bearing housings (oil lubricated) | 90 | 180 | 365 | ISO 4406 above target, water > 500 ppm Alert | ISO 4406, ASTM D7720 | Y
Centrifugal process pump | OHE | Motor and coupling overheating | Infrared | Thermography of motor and coupling | 90 | 180 | 365 | dT limits per ISO 18434-1 | ISO 18434-1 | Y
Centrifugal process pump | ELP | Mechanical seal leakage (acid, H2O2, eluate) | Visual | CM sensitive inspection incl. seal, flange and drain check | 30 | 60 | 90 | Acid or H2O2 leak = Danger | Site, ASME PCC-1 | Y
Positive displacement pump | ELP | Hose / stator / diaphragm wear and leakage | Visual | CM sensitive inspection: hose or stator condition, leaks, pulsation | 30 | 60 | 90 | Leak or hose bulge = Danger | OEM | Y
Positive displacement pump | NOI | Gearbox wear | Vibration | Gearbox and motor vibration route | 60 | 90 | 180 | Velocity Alert 4.5 / Danger 7.1 mm/s; gear-mesh sidebands | ISO 20816-3 | Y
Positive displacement pump | OHE | Gearbox lubricant degradation | Lubrication / oil | Gearbox oil analysis (Fe, PQ, water, viscosity) | 180 | 365 | 365 | Lab limits; PQ trend | ISO 4406, ASTM D7720 | Y
Agitator | NOI | Gear and bearing wear in gearbox | Vibration | Gearbox and motor vibration (velocity, envelope, gear-mesh) | 30 | 60 | 90 | Velocity Alert 4.5 / Danger 7.1 mm/s; GMF sidebands rising | ISO 20816-3, ISO 13373-1 | Y
Agitator | OHE | Gearbox lubricant degradation, water ingress | Lubrication / oil | Gearbox oil analysis (Fe, PQ, Cu, water, viscosity, ISO 4406) | 90 | 90 | 180 | Lab limits; Fe or PQ doubling = Alert | ISO 4406, ASTM D7720 | Y
Agitator | BRD | Shaft, coupling and impeller damage; looseness | Visual | CM sensitive inspection: shaft run-out, coupling, mounting, noise | 30 | 60 | 90 | Visible run-out or loose mounting = Alert | OEM | Y
Agitator | STD | Bridge / support corrosion and fatigue | Structural | Structural inspection of agitator bridge and supports | 365 | 365 | 730 | Section loss > 10% or cracks = Alert | Site, API 571 fatigue | Y
Agitator | OHE | Motor overheating | Infrared | Thermography of motor and gearbox | 90 | 180 | 365 | dT limits per ISO 18434-1 | ISO 18434-1 | Y
Vibrating / linear screen | VIB | Exciter bearing wear, stroke / orbit deviation | Vibration | Exciter bearings, stroke and orbit measurement | 30 | 60 | 90 | Stroke outside OEM band or bearing gE rising = Alert | OEM, ISO 13373-1 | Y
Vibrating / linear screen | STD | Side-plate and cross-beam fatigue cracking | Structural | Crack inspection (visual + MT/PT at hot spots) | 90 | 180 | 180 | Any crack = Danger on load-bearing members | Site, API 571 fatigue | Y
Vibrating / linear screen | OHE | Exciter lubricant degradation | Lubrication / oil | Exciter oil analysis | 90 | 180 | 180 | Lab limits | ISO 4406 | Y
Vibrating / linear screen | PLU | Deck blinding, panel wear and damage | Visual | CM sensitive inspection of decks, panels and springs | 30 | 60 | 90 | Holes in panels or broken springs = Alert | OEM | Y
Crusher / sizer / feeder | VIB | Bearing and drive train wear | Vibration | Vibration route on motor, gearbox and shaft bearings | 30 | 60 | 90 | Alert 4.5 / Danger 7.1 mm/s (rigid); trend for low speed | ISO 20816-3 | Y
Crusher / sizer / feeder | OHE | Gearbox lubricant degradation | Lubrication / oil | Gearbox oil analysis | 90 | 180 | 180 | Lab limits | ISO 4406, ASTM D7720 | Y
Crusher / sizer / feeder | OHE | Brake motor, end shield and coupling overheating | Infrared | Thermography of motors, brakes, couplings | 90 | 180 | 365 | dT limits per ISO 18434-1 | ISO 18434-1 | Y
Crusher / sizer / feeder | STD | Frame, apron pans and wear-part damage | Visual | CM sensitive inspection: wear parts, frame, fasteners | 30 | 60 | 90 | Cracks or loose fasteners = Alert | OEM | Y
Mill drive (SAG / ball) | VIB | Pinion, gearbox, motor bearing wear | Vibration | Vibration route on motor, gearbox, pinion bearings | 14 | 30 |  | OEM / ISO 20816-3 limits; GMF sidebands | ISO 20816-3, ISO 13373-1 | Y
Mill drive (SAG / ball) | OHE | Gearbox and trunnion lube degradation | Lubrication / oil | Oil analysis: gearbox, lube system, trunnion | 30 | 60 |  | Lab limits; ISO 4406 target | ISO 4406, ASTM D7720 | Y
Mill drive (SAG / ball) | OHE | Girth gear load distribution, lubrication | Infrared | Girth gear temperature profile across face width | 30 | 60 |  | Face temperature difference > 10 C Alert | OEM, ISO 18434-1 | Y
Mill drive (SAG / ball) | STD | Shell, liner bolts and trunnion | Visual | CM inspection: liner bolt leaks, shell cracks, trunnion seals | 30 | 30 |  | Liner bolt leak = Alert; shell crack = Danger | OEM | Y
Belt / screw conveyor | STD | Belt damage, splice failure, misalignment | Visual | CM sensitive inspection: belt, splices, tracking, idlers, chutes | 30 | 60 | 90 | Splice damage or tracking off = Alert | Site | Y
Belt / screw conveyor | OHE | Idler and pulley bearing failure | Infrared | Thermography of idlers and pulley bearings | 90 | 180 | 365 | Hot idler = Alert | ISO 18434-1 | Y
Belt / screw conveyor | NOI | Drive gearbox wear | Vibration | Drive gearbox and motor vibration | 60 | 90 | 180 | Alert 4.5 / Danger 7.1 mm/s | ISO 20816-3 | Y
Thickener drive | OHE | Drive gearbox lubricant degradation, wear | Lubrication / oil | Drive oil analysis (low speed: oil is the primary technique) | 90 | 180 | 180 | Lab limits; Fe / PQ trend | ISO 4406, ASTM D7720 | Y
Thickener drive | PDE | Rake torque high, bogging | Visual | CM inspection: torque trend, rake lift, drive noise | 30 | 60 | 90 | Torque > 70% rated sustained = Alert | OEM | Y
Thickener drive | STD | Bridge and feedwell corrosion | Structural | Structural inspection of bridge, walkway, feedwell | 365 | 365 | 730 | Section loss or cracks = Alert | Site | Y
Fan / blower | VIB | Unbalance, bearing wear, looseness | Vibration | Vibration route (main acid plant blower: monthly minimum, online preferred) | 30 | 60 | 90 | ISO 14694 / ISO 20816-3 zones | ISO 14694, ISO 20816-3 | Y
Fan / blower | OHE | Bearing lubricant degradation | Lubrication / oil | Oil analysis (oil lubricated bearings / lube system) | 90 | 180 | 365 | Lab limits | ISO 4406 | Y
Fan / blower | OHE | Motor and bearing overheating | Infrared | Thermography of motor and bearings | 90 | 180 | 365 | dT limits | ISO 18434-1 | Y
Gearbox (stand-alone) | NOI | Gear and bearing wear | Vibration | Vibration route incl. gear-mesh analysis | 30 | 60 | 90 | GMF sidebands, velocity zones | ISO 20816-3, ISO 13373-1 | Y
Gearbox (stand-alone) | OHE | Lubricant degradation | Lubrication / oil | Oil analysis | 90 | 180 | 365 | Lab limits | ISO 4406, ASTM D7720 | Y
Hydraulic / lube unit | ELU | Contamination, wear debris, leakage | Lubrication / oil | Oil analysis with particle count | 90 | 180 | 365 | ISO 4406 above target code = Alert | ISO 4406 | Y
Hydraulic / lube unit | ELU | Hose and fitting leakage | Visual | CM inspection: leaks, filter dP, accumulator | 30 | 60 | 90 | Active leak = Alert | Site | Y
Filter (drum / plate / belt) | PLU | Media blinding, cloth damage | Visual | CM inspection: cloth, cake, sprays, tracking | 30 | 60 | 90 | Torn cloth = Alert | OEM | Y
Filter (drum / plate / belt) | NOI | Drive wear | Vibration | Drive gearbox vibration | 60 | 90 | 180 | Velocity zones | ISO 20816-3 | Y
Electric motor and drive | OHE | Connection, winding and bearing overheating | Infrared | Thermography of terminal boxes and frame | 90 | 180 | 365 | NETA MTS dT: > 4 C Alert, > 15 C Danger | ISO 18434-1, NETA MTS | Y
Electric motor and drive | BRD | Insulation degradation | Electrical | Insulation resistance and polarisation index | 365 | 730 | 730 | IR < 100 MOhm or PI < 2 = Alert | IEEE 43 | Y
Electric motor and drive | VIB | Bearing wear, soft foot | Vibration | Vibration with driven machine | 30 | 60 | 90 | Velocity zones | ISO 20816-3 | Y
Atmospheric storage tank | ELP | Leaks, external corrosion, settlement signs | Visual | Routine in-service external visual walk-down | 30 | 30 | 30 | Leak = Danger; new corrosion or settlement = Alert | API 653 (routine in-service inspection) | Y
Atmospheric storage tank | STD | Shell and roof wall thinning | Ultrasonic thickness | UT at CMLs; baseline + 1 year, then lesser of RL/2 and 5 years | 365 | 365 | 730 | Below t-min = Danger; red band = Alert | API 653, API 571 | Y
Atmospheric storage tank | STD | Formal external inspection by authorised inspector | Tank & vessel | Formal external inspection | 1825 | 1825 | 1825 | Per inspector report | API 653 | Y
Atmospheric storage tank | STD | Foundation, settlement, anchorage | Structural | Foundation, settlement and verticality survey | 365 | 730 | 730 | Tilt or settlement outside API 653 Annex B = Danger | API 653 Annex B | Y
Atmospheric storage tank | ELP | Coating and lining breakdown | Tank & vessel | Coating DFT survey; lining holiday test at internal inspection | 365 | 730 | 730 | DFT < 200 um = Alert; lining holiday = Alert | ISO 12944, NACE SP0188 | Y
Process vessel (atmospheric, lined) | ELP | Leaks, flange and manway gasket failure | Visual | Routine external visual walk-down incl. bolted joints | 30 | 30 | 60 | Active leak = Danger | API 653 practice, ASME PCC-1 | Y
Process vessel (atmospheric, lined) | STD | Formal external inspection | Tank & vessel | Formal external visual inspection (statutory) | 365 | 365 | 730 | Per inspector report | Site statutory, API 510/653 practice | Y
Process vessel (atmospheric, lined) | STD | Wall thinning, roof corrosion | Ultrasonic thickness | UT at CMLs (roof and shell) | 365 | 730 | 730 | Below t-min = Danger | API 571, API 653 practice | Y
Process vessel (atmospheric, lined) | STD | Supports, plinths and anchor bolts (acid attack) | Structural | Structural inspection of supports and plinths | 365 | 365 | 730 | Loss of anchorage = Danger | Site | Y
Pressure vessel / boiler | STD | Statutory inspection and certificate | Statutory | Statutory inspection / hydrotest by competent person | 365 | 365 | 365 | Certificate expired = Danger | Site regulation, API 510 | Y
Pressure vessel / boiler | STD | Wall thinning, boiler tube corrosion | Ultrasonic thickness | UT of shell, heads and tubes (WHB, economiser) | 365 | 365 | 730 | Below minimum = Danger | API 510, API 571 | Y
Pressure vessel / boiler | ELP | Leaks, safety valve condition | Visual | Routine external visual walk-down incl. PSV tags | 30 | 30 | 60 | Leak or PSV overdue = Danger | API 510, API 576 | Y
Piping (acid / slurry / process) | STD | Wall thinning (erosion-corrosion, sulfuric acid corrosion) | Ultrasonic thickness | UT at CMLs, elbows and tees first | 180 | 365 | 1825 | Below minimum = Danger; RL <= 3 years = Alert | API 570, API 571 | Y
Piping (acid / slurry / process) | ELP | Leaks, supports, external corrosion | Piping | External visual inspection of piping circuit | 90 | 180 | 365 | Leak = Danger | API 570 | Y
Sulphur furnace / refractory-lined equipment | OHE | Refractory loss, hot spots | Infrared | Shell thermography scan | 30 | 30 |  | Shell above design or rising hot spot = Alert; above limit = Danger | API RP 936, ISO 18434-1 | Y
Sulphur furnace / refractory-lined equipment | STD | Casing, burner and nozzle condition | Visual | CM inspection incl. burner, sight glasses, expansion joints | 30 | 30 |  | Casing hot spot or leak = Alert | Site | Y
Sulphur furnace / refractory-lined equipment | STD | Structural supports | Structural | Structural inspection of supports and platforms | 365 | 365 |  | Cracks or section loss = Alert | Site | Y
Converter / gas ducts | OHE | Flange leaks, insulation and refractory damage | Infrared | Thermography of beds, flanges and ducts | 30 | 60 |  | Flange dT > 30 C over baseline Alert | ISO 18434-1 | Y
Converter / gas ducts | STD | Duct and economiser dew-point corrosion | Ultrasonic thickness | UT of ducts below acid dew point and economiser | 365 | 730 |  | Below minimum = Danger | API 571 | Y
Drying / absorption tower, acid cooler and acid piping | STD | Sulfuric acid corrosion (velocity, temperature, concentration) | Ultrasonic thickness | UT of acid lines, cooler shells, tower shell at CMLs | 180 | 365 |  | Below minimum = Danger; ST rate > 1.5 x LT = Alert | API 571 sulfuric acid corrosion | Y
Drying / absorption tower, acid cooler and acid piping | INL | Anodic protection / cooler tube leak | Electrical | Anodic protection potential check and cooler leak detection | 7 | 7 |  | Potential outside OEM band = Alert | OEM | Y
Drying / absorption tower, acid cooler and acid piping | OHE | Brick lining failure, hot spots | Infrared | Tower shell thermography | 90 | 180 |  | Hot spot = Alert | ISO 18434-1 | Y
Drying / absorption tower, acid cooler and acid piping | ELP | Acid leaks at flanges and pumps | Visual | Routine walk-down of acid circuit | 30 | 30 |  | Any acid leak = Danger | Site, ASME PCC-1 | Y
Switchgear / MCC / transformer | OHE | Loose or corroded connections | Infrared | Thermography under load (> 40% load) | 90 | 180 | 365 | NETA MTS: > 4 C Alert, > 15 C Danger | NETA MTS, NFPA 70B, ISO 18434-1 | Y
Switchgear / MCC / transformer | BRD | Partial discharge, tracking | Ultrasonics (airborne) | Airborne ultrasound / TEV partial discharge survey | 180 | 365 | 365 | PD activity detected = Alert | IEC 62478 practice | Y
Switchgear / MCC / transformer | BRD | Transformer insulation and oil degradation | Lubrication / oil | Transformer oil DGA and quality | 365 | 365 | 730 | DGA per IEC 60599 / IEEE C57.104 | IEC 60599, IEEE C57.104 | Y
Rotary dryer / kiln / calciner | OHE | Refractory loss, shell hot spots | Infrared | Shell thermography scan | 30 | 30 |  | Shell above limit = Danger | API RP 936, ISO 18434-1 | Y
Rotary dryer / kiln / calciner | VIB | Drive train wear | Vibration | Drive vibration route | 30 | 60 |  | Velocity zones | ISO 20816-3 | Y
Rotary dryer / kiln / calciner | OHE | Girth gear lubrication | Lubrication / oil | Girth gear lubricant check and oil analysis | 90 | 90 |  | Lab limits | OEM | Y
Rotary dryer / kiln / calciner | STD | Tyre and roller alignment, shell ovality | Structural | Alignment and ovality survey | 365 | 365 |  | Out of OEM tolerance = Alert | OEM | Y
Diesel generator | OHE | Turbocharger, exhaust and cooling deviation | DG checks | Daily log: exhaust temp per cylinder, turbo in/out, oil pressure, coolant temp | 1 | 1 | 7 | Exhaust spread > 50 C or turbo outlet above OEM = Alert | OEM | Y
Diesel generator | OHE | Engine wear, fuel dilution, coolant ingress | Lubrication / oil | Engine oil analysis every 250 running hours (approx. monthly) | 30 | 30 | 60 | Lab limits (Fe, Si, Na/K, fuel dilution) | OEM, ASTM D7720 | Y
Diesel generator | VIB | Alternator and engine mounting | Vibration | Vibration of alternator bearings and engine mounts | 30 | 60 | 90 | ISO 8528-9 limits | ISO 8528-9 | Y
Diesel generator | OHE | Exhaust, turbo lagging, electrical connections | Infrared | Thermography of exhaust, turbo lagging and terminals | 90 | 90 | 180 | Lagging gaps / hot spots = Alert | ISO 18434-1 | Y
Baghouse / dust collector | PDE | Bag blinding, broken bags, pulse-jet failure | Visual | Differential pressure log, bag leak detector trend, pulse valve function, hopper discharge | 30 | 30 | 60 | dP outside OEM band or leak detector alarm = Alert; visible emission = Danger | OEM, site emission licence | Y
Baghouse / dust collector | ELU | Compressed air and pulse valve leaks | Ultrasonics (airborne) | Ultrasound survey of pulse valves, headers and seals | 90 | 180 | 365 | Leak detected = Alert | ISO 29821 | Y
Baghouse / dust collector | STD | Housing and hopper corrosion, door seal leaks (product dust) | Tank & vessel | Housing, hopper and door seal inspection (radiological work permit) | 365 | 365 | 730 | Seal leak or hole = Danger in product area | Site, radiation management plan | Y
Stack / emission point | PDE | Particulate and uranium emissions above licence | Statutory | Stack emission monitoring as required by the licence | 90 | 90 | 180 | Above licence limit = Danger | Site emission licence | Y
Stack / emission point | STD | Stack shell corrosion, supports, sampling ports | Structural | Stack structural inspection and UT at base | 365 | 730 | 730 | Section loss or crack = Alert | Site | Y
Feeder / vibrator (product handling) | VIB | Bearing wear, unbalance, loose mounting | Vibration | Vibration route on drives and vibrator motors | 60 | 90 | 180 | Velocity zones | ISO 20816-3 | Y
Feeder / vibrator (product handling) | BRD | Rotary valve wear, seal leakage of product dust | Visual | CM inspection: rotor clearance, seals, flexible connections | 30 | 60 | 90 | Product leak = Danger | OEM, radiation management plan | Y
Feeder / vibrator (product handling) | OHE | Motor and bearing overheating | Infrared | Thermography of motors and bearings | 90 | 180 | 365 | dT limits | ISO 18434-1 | Y
Product packaging line | SER | Drum filling, sealing, washing and weighing faults | Visual | CM inspection of filling head, lid press, drum washer, check-weigher and conveyors | 30 | 60 | 90 | Product spillage or seal failure = Danger | OEM, radiation management plan | Y
Product packaging line | AIR | Check-weigher accuracy (product accountancy) | Electrical | Check-weigher calibration with certified weights | 90 | 90 | 180 | Outside tolerance = Alert | Site product accountancy / safeguards | Y
Product packaging line | OHE | Drive and motor overheating | Infrared | Thermography of drives and motors | 90 | 180 | 365 | dT limits | ISO 18434-1 | Y
Heat exchanger / condenser | ELP | Tube or gasket leakage | Visual | CM inspection: leaks, vent, drains | 30 | 60 | 90 | Leak = Alert; acid or product leak = Danger | Site | Y
Heat exchanger / condenser | PDE | Fouling, loss of performance | Infrared | Inlet and outlet temperature survey (approach temperature) | 90 | 180 | 365 | Approach rising over 25% from baseline = Alert | OEM, ISO 18434-1 | Y
Heat exchanger / condenser | STD | Shell and nozzle wall thinning | Ultrasonic thickness | UT of shell, nozzles and channels | 365 | 730 | 730 | Below minimum = Danger | API 571, API 510 practice | Y
Sump / bund (concrete) | STD | Concrete acid attack, lining failure, cracks | Structural | Inspection of sump or bund concrete and lining | 180 | 365 | 365 | Exposed reinforcement or lining breach = Alert; leak path = Danger | Site, ISO 12944 / acid-resistant lining practice | Y
Sump / bund (concrete) | ELP | Overflow and containment loss | Visual | CM inspection: level control, pump-out, overflow route | 30 | 60 | 90 | Overflow evidence = Alert | Site | Y
Bin / chute / bunker | STD | Liner and wall wear, holes, hang-ups | Visual | CM inspection of liners, wear plates, flow and level devices | 90 | 180 | 365 | Hole in wall or liner = Alert | Site | Y
Bin / chute / bunker | STD | Wall thinning at impact zones | Ultrasonic thickness | UT at impact and wear zones | 365 | 730 | 730 | Below minimum = Danger | Site | Y
Bin / chute / bunker | STD | Support structure and hopper connections | Structural | Structural inspection of supports and bolting | 365 | 730 | 730 | Cracks or section loss = Alert | Site | Y

## Standards_Map
Standards compliance map
How AHIM implements each standard and what remains to be done.
Standard | Clause | Requirement | AHIM implementation | Status
ISO 55001:2014 | 4-10 | Asset management system: context, leadership, planning, support, operation, evaluation, improvement | Framework document; Management page; monthly review and commentary; roadmap | Partial: SAMP and management review to formalise
ISO 55001:2014 | 6.2 | Asset management objectives and plans | KPI targets in Lists; Management page vs target | In place
ISO 55001:2014 | 7.5 | Documented information and data | Asset_Register, common record format, data dictionary, validation | In place
ISO 55001:2014 | 9.1 | Monitoring, measurement, analysis and evaluation | AHI, data confidence, strategy compliance, SMRP metrics | In place
ISO 55001:2014 | 10.1 | Nonconformity and corrective action | Open recommendations, ageing, overdue, escalation, RCA on bad actors | In place
ISO 31000:2018 | 6.4 | Risk assessment (identification, analysis, evaluation) | 5x5 risk matrix, Risk page, risk register | In place
ISO 14224:2016 | 8, Annex B | Equipment taxonomy, failure modes and mechanisms | ISO 14224 failure mode and mechanism fields; site mapping | In place: hierarchy to maintainable item level to complete
ISO 17359:2018 | 5-7 | Condition monitoring programme: failure mode, technique, interval, alarm | Strategy library with intervals and criteria; strategy compliance | In place
ISO 18436 series | - | Competence of CM personnel | Competence matrix in framework document | To implement
ISO 20816-3 / ISO 13373 | - | Vibration evaluation and analysis | Vibration limits 4.5 / 7.1 mm/s; strategy tasks | In place
ISO 18434-1 | - | Thermography for condition monitoring | IR tasks and NETA dT limits | In place
ISO 29821 | - | Ultrasound for condition monitoring | Ultrasound tasks | In place
ISO 4406 / ASTM D7720 | - | Oil cleanliness and oil analysis alarm limits | Oil analysis tasks and lab limits | In place
API 653 | 6 | Tank inspection intervals, remaining life | Thickness monitoring, remaining life, next UT due | Partial: t-min per shell course to calculate
API 570 / API 510 | 6-7 | Piping and pressure vessel inspection | Piping and vessel strategy tasks; statutory register | Partial: piping CML programme to set up
API 571 | - | Damage mechanisms | Damage mechanism field and library | In place
API 580 / 581 | - | Risk-based inspection | Likelihood from remaining life and damage mechanism | Partial: semi-quantitative RBI to formalise
ASME PCC-1 | - | Bolted flange joint assembly | Flange leak actions (vessel inspections) | Procedure to adopt
SMRP Best Practice Metrics | - | Maintenance and reliability KPIs | Planned vs reactive work, PM completion, backlog | In place (from Pronto WO export)
ICRP / IAEA radiation protection | - | ALARA for maintenance on uranium-bearing equipment | Consequence category Health and radiation; framework document | In place in risk matrix